## Notch Filter Design
Rev: 7-27-2020 | [10 empty] | Click here to learn how to use this spreadsheet tool. You will be redirected to our YouTube Channel: https://youtu.be/sV6w9_-4ZJw | [23 empty] | PLOT (ohms) |  |  | (res branch) | (aux branch) | product of res branch and aux branch | sum of res branch and aux branch | power over sum rule of aux and res branch | add main cap in |  |  | SD - Standard Duty Capacitors, with -40C to +55C Temperature Rating
[34 empty] | HARM # | Xc main | Xc aux | XL (inductance) | Resistance | XCAUX + XL | [6 empty] | HD- Heavy Duty Capacitors, with -40C to +55C Temperature Rating
Northeast Power Systems, Inc. | [10 empty] | Contact NEPSI for assistance or to obtain a quote on your metal-enclosed harmonic filter system. Email us at: sales@nepsi.com | [22 empty] | 1 | 0.0001-342.375298606877i | 0.000000001 | 0.154991081306871+15.4991081306871i | 9999999999+9999999i | 0.154991082306871+15.4991081306871i | 1394919757.10596+154992631202.04i | 9999999999.15499+10000014.4991081i | 0.1549911063262+15.4991081301826i | 0.1550911063262-326.876190476694i | 1 | 326.8762 | EXD - Extreme Duty Capacitors, with -50C to +55C Temperature Rating
66 Carey Road, Queensbury, NY |  |  |  |  | Phone: (518) 792-4776 Fax: (518) 792-5767 www.nepsi.com | [28 empty] | 1.2 | 0.0001-285.312748839065i | 0.000000001 | 0.154991081306871+18.5989297568245i | 9999999999+9999999i | 0.154991082306871+18.5989297568245i | 1363921543.9444+185990847460.314i | 9999999999.15499+10000017.5989298i | 0.154991116895876+18.5989297562134i | 0.155091116895876-266.713819082852i | 1.2 | 266.7139
[34 empty] | 1.4 | 0.0001-244.553784719198i | 0.000000001 | 0.154991081306871+21.6987513829619i | 9999999999+9999999i | 0.154991082306871+21.6987513829619i | 1332923330.78285+216989063718.588i | 9999999999.15499+10000020.6987514i | 0.15499112938733+21.6987513822422i | 0.15509112938733-222.855033336956i | 1.4 | 222.8551
FILTER BANK DESIGN CALCULATIONS - NOTCH FILTER DESIGN | [10 empty] | REVERSE CALCULATION USING C AND L | [22 empty] | 1.6 | 0.0001-213.984561629298i | 0.000000001 | 0.154991081306871+24.7985730090993i | 9999999999+9999999i | 0.154991082306871+24.7985730090993i | 1301925117.6213+247987279976.863i | 9999999999.15499+10000023.798573i | 0.154991143800561+24.7985730082691i | 0.155091143800561-189.185988621029i | 1.6 | 189.1861
[34 empty] | 1.8 | 0.0001-190.208499226043i | 0.000000001 | 0.154991081306871+27.8983946352367i | 9999999999+9999999i | 0.154991082306871+27.8983946352367i | 1270926904.45975+278985496235.137i | 9999999999.15499+10000026.8983946i | 0.154991160135569+27.8983946342941i | 0.155091160135569-162.310104591749i | 1.8 | 162.3102
kVLLsys (System Line-to-Line Voltage Rating) |  | 26.2 | kV |  |  | Job Name: | Enter Job Name |  |  |  | CAPACITANCE (µf) | 11.46 | (µf) | [20 empty] | 2 | 0.0001-171.187649303439i | 0.000000001 | 0.154991081306871+30.9982162613741i | 9999999999+9999999i | 0.154991082306871+30.9982162613741i | 1239928691.29819+309983712493.411i | 9999999999.15499+10000029.9982163i | 0.154991178392353+30.9982162603171i | 0.155091178392353-140.189433043122i | 2 | 140.1895
Qeff (3-Phase Output Rating of Filter) |  | 2100 | kvar |  |  | Stage/Branch Name | Branch/Stage # |  |  |  | INDUCTANCE (mH) | 23 | mH | [20 empty] | 2.2 | 0.0001-155.625135730399i | 0.000000001 | 0.154991081306871+34.0980378875116i | 9999999999+9999999i | 0.154991082306871+34.0980378875116i | 1208930478.13664+340981928751.686i | 9999999999.15499+10000033.0980379i | 0.154991198570914+34.0980378863384i | 0.155091198570914-121.527097844061i | 2.2 | 121.5272
h (Tuning Point of Filter) |  | 4.7 | (harmonic #) | [7 empty] | XL (Ohms) | 8.6705 | Ohms |  |  |  |  | EasyPower Input - Filter Input Data | [15 empty] | 2.4 | 0.0001-142.656374419532i | 0.000000001 | 0.154991081306871+37.197859513649i | 9999999999+9999999i | 0.154991082306871+37.197859513649i | 1177932264.97509+371980145009.96i | 9999999999.15499+10000036.1978595i | 0.154991220671253+37.1978595123576i | 0.155091220671253-105.458514907174i | 2.4 | 105.4586
f (System Frequency) |  | 60 | (HZ) | [5 empty] | Tuning Point for loss of one capacitror: | 6.65 | Xc (Ohms) | 231.4713 | Ohms | [20 empty] | 2.6 | 0.0001-131.682807156491i | 0.000000001 | 0.154991081306871+40.2976811397864i | 9999999999+9999999i | 0.154991082306871+40.2976811397864i | 1146934051.81354+402978361268.234i | 9999999999.15499+10000039.2976811i | 0.154991244693368+40.2976811383748i | 0.155091244693368-91.3851260181162i | 2.6 | 91.3853
hFrequency |  | 282 | Hz | [7 empty] | h (Tuning Point) | 5.1668 | [6 empty] | Resistor |  |  | Ohms | [11 empty] | 2.8 | 0.0001-122.276892359599i | 0.000000001 | 0.154991081306871+43.3975027659238i | 9999999999+9999999i | 0.154991082306871+43.3975027659238i | 1115935838.65198+433976577526.509i | 9999999999.15499+10000042.3975028i | 0.15499127063726+43.3975027643903i | 0.15509127063726-78.8793895952087i | 2.8 | 78.8795
Xeff (effective reactance of Filter Bank) |  | 326.8762 | Ohms | [15 empty] | Inductor | 0.15499 |  | + j | 15.4991 |  | Ohms | [8 empty] | 3 | 0.0001-114.125099535626i | 0.000000001 | 0.154991081306871+46.4973243920612i | 9999999999+9999999i | 0.154991082306871+46.4973243920612i | 1084937625.49043+464974793784.783i | 9999999999.15499+10000045.4973244i | 0.154991298502929+46.4973243904037i | 0.155091298502929-67.6277751452223i | 3 | 67.628
IRATED FUNDAMENTAL |  | 46.331 | amps | [7 empty] | Qeff | 3.081 | MVAR | [5 empty] | Capacitor Bank 1: | 2.5323 |  | MVAR @ | 29.41 |  | kV (LL) | [8 empty] | 3.2 | 0.0001-106.992280814649i | 0.000000001 | 0.154991081306871+49.5971460181986i | 9999999999+9999999i | 0.154991082306871+49.5971460181986i | 1053939412.32888+495973010043.057i | 9999999999.15499+10000048.597146i | 0.154991328290375+49.5971460164152i | 0.155091328290375-57.3951347982338i | 3.2 | 57.3953
IFILTER RMS CURRENT |  | 108.4 | amps | [15 empty] | Capacitor Bank 1: |  |  | MVAR @ |  |  | kV (LL) | [8 empty] | 3.4 | 0.0001-100.698617237317i | 0.000000001 | 0.154991081306871+52.6969676443361i | 9999999999+9999999i | 0.154991082306871+52.6969676443361i | 1022941199.16733+526971226301.332i | 9999999999.15499+10000051.6969676i | 0.154991359999598+52.6969676424249i | 0.155091359999598-48.0016495948921i | 3.4 | 48.0019
[11 empty] | CAPACITANCE CALCULATOR - Single-Phase Calculator | [22 empty] | 3.6 | 0.0001-95.1042496130215i | 0.000000001 | 0.154991081306871+55.7967892704735i | 9999999999+9999999i | 0.154991082306871+55.7967892704735i | 991942986.005773+557969442559.606i | 9999999999.15499+10000054.7967893i | 0.154991393630597+55.7967892684326i | 0.155091393630597-39.3074603445889i | 3.6 | 39.3078
[34 empty] | 3.8 | 0.0001-90.0987627912835i | 0.000000001 | 0.154991081306871+58.8966108966109i | 9999999999+9999999i | 0.154991082306871+58.8966108966109i | 960944772.844221+588967658817.88i | 9999999999.15499+10000057.8966109i | 0.154991429183374+58.8966108944383i | 0.155091429183374-31.2021518968452i | 3.8 | 31.2025
[11 empty] | CAPACITOR KVAR | 490 | kvar | [20 empty] | 4 | 0.0001-85.5938246517194i | 0.000000001 | 0.154991081306871+61.9964325227483i | 9999999999+9999999i | 0.154991082306871+61.9964325227483i | 929946559.682668+619965875076.155i | 9999999999.15499+10000060.9964325i | 0.154991466657927+61.9964325204422i | 0.155091466657927-23.5973921312772i | 4 | 23.5979
[11 empty] | CAPACITOR FREQUENCY | 60 | Hertz | [20 empty] | 4.2 | 0.0001-81.5179282397327i | 0.000000001 | 0.154991081306871+65.0962541488857i | 9999999999+9999999i | 0.154991082306871+65.0962541488857i | 898948346.521116+650964091334.429i | 9999999999.15499+10000064.0962541i | 0.154991506054257+65.0962541464441i | 0.155091506054257-16.4216740932886i | 4.2 | 16.4224
[11 empty] | CAPACITOR VOLTAGE (kV) | 9.96 | kV | [20 empty] | 4.4 | 0.0001-77.8125678651994i | 0.000000001 | 0.154991081306871+68.1960757750231i | 9999999999+9999999i | 0.154991082306871+68.1960757750231i | 867950133.359564+681962307592.703i | 9999999999.15499+10000067.1960758i | 0.154991547372365+68.1960757724441i | 0.155091547372365-9.61649209275529i | 4.4 | 9.6177
[11 empty] | CAPACITANCE (µf) | 13.1 | (µf) | [20 empty] | 4.6 | 0.0001-74.4294127406255i | 0.000000001 | 0.154991081306871+71.2958974011606i | 9999999999+9999999i | 0.154991082306871+71.2958974011606i | 836951920.19801+712960523850.978i | 9999999999.15499+10000070.2958974i | 0.154991590612249+71.2958973984422i | 0.155091590612249-3.1335153421833i | 4.6 | 3.1374
Xc |  | 342.3753 | Ohms | [5 empty] | Capacitance (per phase): | 7.75 micro-farads/Phase | Xc (Ohms) | 202.4522 | Ohms | [20 empty] | 4.8 | 0.0001-71.3281872097661i | 0.000000001 | 0.154991081306871+74.395719027298i | 9999999999+9999999i | 0.154991082306871+74.395719027298i | 805953707.036458+743958740109.252i | 9999999999.15499+10000073.395719i | 0.15499163577391+74.3957190244384i | 0.15509163577391+3.06753181467231i | 4.8 | 3.0714
[11 empty] | RATED CURRENT | 49.1968 | AMPS | [20 empty] | 5 | 0.0001-68.4750597213755i | 0.000000001 | 0.154991081306871+77.4955406534354i | 9999999999+9999999i | 0.154991082306871+77.4955406534354i | 774955493.874906+774956956367.526i | 9999999999.15499+10000076.4955407i | 0.154991682857349+77.4955406504326i | 0.155091682857349+9.0204809290571i | 5 | 9.0218
XL (Inductive reactance of reactor at system frequency) |  | 15.4991 | ohms | [30 empty] | 5.2 | 0.0001-65.8414035782456i | 0.000000001 | 0.154991081306871+80.5953622795728i | 9999999999+9999999i | 0.154991082306871+80.5953622795728i | 743957280.713353+805955172625.801i | 9999999999.15499+10000079.5953623i | 0.154991731862563+80.595362276425i | 0.155091731862563+14.7539586981794i | 5.2 | 14.7548
H (Inductance of Reactor) |  | 41.1139 | mH | [7 empty] | Tuning Point Based on Reactor % | [22 empty] | 5.4 | 0.0001-63.4028330753477i | 0.000000001 | 0.154991081306871+83.6951839057102i | 9999999999+9999999i | 0.154991082306871+83.6951839057102i | 712959067.551801+836953388884.075i | 9999999999.15499+10000082.6951839i | 0.154991782789555+83.6951839024153i | 0.155091782789555+20.2923508270676i | 5.4 | 20.2929
XX/R RATIO (X/R OF IRON-CORE REACTOR AT FUNDAMENTAL FREQUENCY) |  | 100 | Typically Near 100 | [30 empty] | 5.6 | 0.0001-61.1384461797995i | 0.000000001 | 0.154991081306871+86.7950055318477i | 9999999999+9999999i | 0.154991082306871+86.7950055318477i | 681960854.390247+867951605142.35i | 9999999999.15499+10000085.7950055i | 0.154991835638323+86.7950055284039i | 0.155091835638323+25.6565593486044i | 5.6 | 25.657
[11 empty] | Reactor % | 7 | (%) | [20 empty] | 5.8 | 0.0001-59.0302238977375i | 0.000000001 | 0.154991081306871+89.8948271579851i | 9999999999+9999999i | 0.154991082306871+89.8948271579851i | 650962641.228695+898949821400.624i | 9999999999.15499+10000088.8948272i | 0.154991890408869+89.8948271543904i | 0.155091890408869+30.8646032566529i | 5.8 | 30.865
CAPACITOR PARAMETERS | [10 empty] | Tuning Point | 3.7796 | [21 empty] | 6 | 0.0001-57.0625497678129i | 0.000000001 | 0.154991081306871+92.9946487841225i | 9999999999+9999999i | 0.154991082306871+92.9946487841225i | 619964428.067143+929948037658.898i | 9999999999.15499+10000091.9946488i | 0.154991947101192+92.994648780375i | 0.155091947101192+35.9320990125621i | 6 | 35.9324
VCAP RATING |  | 17 | kV | [14 empty] | ETAP Input Data | [15 empty] | 6.2 | 0.0001-55.221822355948i | 0.000000001 | 0.154991081306871+96.0944704102599i | 9999999999+9999999i | 0.154991082306871+96.0944704102599i | 588966214.90559+960946253917.173i | 9999999999.15499+10000095.0944704i | 0.154992005715291+96.0944704063578i | 0.155092005715291+40.8726480504098i | 6.2 | 40.8729
QRATED PER PHASE |  | 844.103 | kvar | [7 empty] | CAPACITANCE CALCULATOR - Three-Phase Calculator | [8 empty] | Capacitor C1 |  |  | Inductor L1 | [10 empty] | 6.4 | 0.0001-53.4961404073246i | 0.000000001 | 0.154991081306871+99.1942920363973i | 9999999999+9999999i | 0.154991082306871+99.1942920363973i | 557968001.744038+991944470175.447i | 9999999999.15499+10000098.194292i | 0.154992066251167+99.1942920323385i | 0.155092066251167+45.6981516250139i | 6.4 | 45.6984
Number of Caps Per Phase (N) |  | 2 | [5 empty] | Main Cap Capacitive Reactance (per can): | 684.7506 | Ohms/Capacitor | [8 empty] | KVAR | 844.103 |  | XL1 | 15.4991 |  | ohms | [8 empty] | 6.6 | 0.0001-51.8750452434663i | 0.000000001 | 0.154991081306871+102.294113662535i | 9999999999+9999999i | 0.154991082306871+102.294113662535i | 526969788.582483+1022942686433.72i | 9999999999.15499+10000101.2941137i | 0.154992128708821+102.294113658317i | 0.155092128708821+50.4190684148507i | 6.6 | 50.4193
Capacitor Can KVAR Rating (kvar) |  | 422.0515 | kvar |  |  |  |  | Main Cap Capacitance (per can): | 3.8739 | µF (micro-farads)/Capacitor | CAPACITOR KVAR (3-Phase) | 75 | kvar | [5 empty] | Uf | 7.75 |  | Q Factor | 100 | [10 empty] | 6.8 | 0.0001-50.3493086186584i | 0.000000001 | 0.154991081306871+105.393935288672i | 9999999999+9999999i | 0.154991082306871+105.393935288672i | 495971575.420934+1053940902691.99i | 9999999999.15499+10000104.3939353i | 0.15499219308825+105.393935284294i | 0.15509219308825+55.0446266656356i | 6.8 | 55.0448
ICAP (Fundamental Amps Each Capacitor) |  | 23.1655 | amps | [7 empty] | CAPACITOR FREQUENCY (HZ) | 60 | Hertz | [5 empty] | Rated kV | 17 |  | Max I | 108.4 |  | Amps | [8 empty] | 7 | 0.0001-48.9107569438396i | 0.000000001 | 0.154991081306871+108.49375691481i | 9999999999+9999999i | 0.154991082306871+108.49375691481i | 464973362.259376+1084939118950.27i | 9999999999.15499+10000107.4937569i | 0.154992259389457+108.493756910269i | 0.155092259389457+59.5829999664294i | 7 | 59.5832
IFUSE (Minimum Recommended Fuse Rating on each Capacitors) |  | 41.6979 | amps | [7 empty] | CAPACITOR VOLTAGE (kV - Line-to-Line) | 0.6 | kV | [5 empty] | Max. KV | 18.7 | [13 empty] | 7.2 | 0.0001-47.5521248065107i | 0.000000001 | 0.154991081306871+111.593578540947i | 9999999999+9999999i | 0.154991082306871+111.593578540947i | 433975149.097827+1115937335208.54i | 9999999999.15499+10000110.5935785i | 0.154992327612441+111.593578536242i | 0.155092327612441+64.0414537297313i | 7.2 | 64.0416
VCAP FUNDAMENTAL VOLTAGE |  | 15.8626 | kV | [7 empty] | CAPACITANCE (µf - Line-to-Neutral) | 552.64 | (µf) | [20 empty] | 7.4 | 0.0001-46.2669322441726i | 0.000000001 | 0.154991081306871+114.693400167084i | 9999999999+9999999i | 0.154991082306871+114.693400167084i | 402976935.936279+1146935551466.81i | 9999999999.15499+10000113.6934002i | 0.154992397757202+114.693400162213i | 0.155092397757202+68.4264679180404i | 7.4 | 68.4266
VCAP RMS VOLTAGE |  | 17.2236 | kV | [7 empty] | Xc (Ohms)/Phase (Y Imp) | 4.8 | Ohms | [20 empty] | 7.6 | 0.0001-45.0493813956418i | 0.000000001 | 0.154991081306871+117.793221793222i | 9999999999+9999999i | 0.154991082306871+117.793221793222i | 371978722.774721+1177933767725.09i | 9999999999.15499+10000116.7932218i | 0.15499246982374+117.793221788183i | 0.15509246982374+72.7438403925412i | 7.6 | 72.744
VPEAK CAP VOLTAGE |  | 31.9184 | kV | [7 empty] | RATED CURRENT | 72.2543 | AMPS | [20 empty] | 7.8 | 0.0001-43.8942690521638i | 0.000000001 | 0.154991081306871+120.893043419359i | 9999999999+9999999i | 0.154991082306871+120.893043419359i | 340980509.613172+1208931983983.36i | 9999999999.15499+10000119.8930434i | 0.154992543812054+120.89304341415i | 0.155092543812054+76.9987743619862i | 7.8 | 76.9989
ICAP RMS CURRENT |  | 54.2 | amps | [7 empty] | Terminal-to-Terminal Reactance (ohms) | 9.6 | Ohms | [20 empty] | 8 | 0.0001-42.7969123258597i | 0.000000001 | 0.154991081306871+123.992865045497i | 9999999999+9999999i | 0.154991082306871+123.992865045497i | 309982296.451614+1239930200241.65i | 9999999999.15499+10000122.992865i | 0.154992619722146+123.992865040116i | 0.155092619722146+81.1959527142563i | 8 | 81.1961
QCAPACITROR (1-phase) |  | 1392.5649 | kvar | [7 empty] | Terminal-to-Terminal Capacitance (uF) | 276.32 | [21 empty] | 8.2 | 0.0001-41.7530851959607i | 0.000000001 | 0.154991081306871+127.092686671634i | 9999999999+9999999i | 0.154991082306871+127.092686671634i | 278984083.290066+1270928416499.92i | 9999999999.15499+10000126.0926867i | 0.154992697554015+127.09268666608i | 0.155092697554015+85.3396014701193i | 8.2 | 85.3397
[34 empty] | 8.4 | 0.0001-40.7589641198664i | 0.000000001 | 0.154991081306871+130.192508297771i | 9999999999+9999999i | 0.154991082306871+130.192508297771i | 247985870.128517+1301926632758.19i | 9999999999.15499+10000129.1925083i | 0.15499277730766+130.192508292041i | 0.15509277730766+89.4335441721746i | 8.4 | 89.4337
CAPACITOR DESIGN RATINGS VS IEEE/ANSI MAXIMUMS | [33 empty] | 8.6 | 0.0001-39.8110812333578i | 0.000000001 | 0.154991081306871+133.292329923909i | 9999999999+9999999i | 0.154991082306871+133.292329923909i | 216987656.966959+1332924849016.47i | 9999999999.15499+10000132.2923299i | 0.154992858983082+133.292329918001i | 0.155092858983082+93.4812486846432i | 8.6 | 93.4814
Capacitor Duty Rating: |  | HD- Heavy Duty Capacitors, with -40C to +55C Temperature Rating | [31 empty] | 8.8 | 0.0001-38.9062839325997i | 0.000000001 | 0.154991081306871+136.392151550046i | 9999999999+9999999i | 0.154991082306871+136.392151550046i | 185989443.80541+1363923065274.74i | 9999999999.15499+10000135.3921515i | 0.154992942580281+136.392151543958i | 0.155092942580281+97.4858676113583i | 8.8 | 97.486
|  | Capacitor Design Values |  |  |  |  | Capacitor Design Values
|  | At Nominal Voltage | At 110% System Voltage | Capacitor Rating |  |  | At Nominal Voltage | At 110% System Voltage |  | Capacitor Rating | [22 empty] | 17 | 9 | 0.0001-38.0416998452086i | 0.000000001 | 0.154991081306871+139.491973176184i | 9999999999+9999999i | 0.154991082306871+139.491973176184i | 154991230.643852+1394921281533.02i | 9999999999.15499+10000138.4919732i | 0.154993028099258+139.491973169915i | 0.155093028099258+101.450273324706i | 9 | 101.4504
% RATED VOLTS (RMS Voltage) |  | 101.3% | 110% | 125% |  | % 60HZ AMPS: | 218.3% | 222.5% |  | 135% | [22 empty] | 24.038 | 9.2 | 0.0001-37.2147063703128i | 0.000000001 | 0.154991081306871+142.591794802321i | 9999999999+9999999i | 0.154991082306871+142.591794802321i | 123993017.482304+1425919497791.29i | 9999999999.15499+10000141.5917948i | 0.15499311554001+142.591794795868i | 0.15509311554001+105.377088425555i | 9.2 | 105.3772
% CREST VOLTAGE (Peak) |  | 132.8% | 142.8% | 135% |  | % 60HZ KVAR: | 165% | 183.3% |  | 135% | [22 empty] | 24.8266 | 9.4 | 0.0001-36.4229041071146i | 0.000000001 | 0.154991081306871+145.691616428458i | 9999999999+9999999i | 0.154991082306871+145.691616428458i | 92994804.3207555+1456917714049.56i | 9999999999.15499+10000144.6916164i | 0.15499320490254+145.69161642182i | 0.15509320490254+109.268712314705i | 9.4 | 109.2688
[33 empty] | 844.103 | 9.6 | 0.0001-35.6640936048831i | 0.000000001 | 0.154991081306871+148.791438054596i | 9999999999+9999999i | 0.154991082306871+148.791438054596i | 61996591.1591971+1487915930307.84i | 9999999999.15499+10000147.7914381i | 0.154993296186848+148.79143804777i | 0.155093296186848+113.127344442887i | 9.6 | 113.1275
[34 empty] | 9.8 | 0.0001-34.9362549598855i | 0.000000001 | 0.154991081306871+151.891259680733i | 9999999999+9999999i | 0.154991082306871+151.891259680733i | 30998377.9976487+1518914146566.11i | 9999999999.15499+10000150.8912597i | 0.154993389392931+151.891259673718i | 0.155093389392931+116.955004713832i | 9.8 | 116.9551
[34 empty] | 10 | 0.0001-34.2375298606878i | 0.000000001 | 0.154991081306871+154.991081306871i | 9999999999+9999999i | 0.154991082306871+154.991081306871i | 164.836090326309+1549912362824.39i | 9999999999.15499+10000153.9910813i | 0.154993484520791+154.991081299665i | 0.155093484520791+120.753551438977i | 10 | 120.7537
[18 empty] | PowerFactory Input - Notch Filter | [15 empty] | 10.2 | 0.0001-33.5662057457723i | 0.000000001 | 0.154991081306871+158.090902933008i | 9999999999+9999999i | 0.154991082306871+158.090902933008i | -30998048.3254583+1580910579082.66i | 9999999999.15499+10000157.0909029i | 0.154993581570428+158.090902925609i | 0.155093581570428+124.524697179837i | 10.2 | 124.5248
[34 empty] | 10.4 | 0.0001-32.9207017891229i | 0.000000001 | 0.154991081306871+161.190724559145i | 9999999999+9999999i | 0.154991082306871+161.190724559145i | -61996261.4870064+1611908795340.93i | 9999999999.15499+10000160.1907246i | 0.154993680541843+161.19072455155i | 0.155093680541843+128.270022762427i | 10.4 | 128.2701
[34 empty] | 10.6 | 0.0001-32.2995564723469i | 0.000000001 | 0.154991081306871+164.290546185283i | 9999999999+9999999i | 0.154991082306871+164.290546185283i | -92994474.6485648+1642907011599.21i | 9999999999.15499+10000163.2905462i | 0.154993781435034+164.290546177491i | 0.155093781435034+131.990989705144i | 10.6 | 131.9911
[34 empty] | 10.8 | 0.0001-31.7014165376739i | 0.000000001 | 0.154991081306871+167.39036781142i | 9999999999+9999999i | 0.154991082306871+167.39036781142i | -123992687.810113+1673905227857.48i | 9999999999.15499+10000166.3903678i | 0.154993884250002+167.390367803429i | 0.155093884250002+135.688951265755i | 10.8 | 135.689
[34 empty] | 11 | 0.0001-31.1250271460798i | 0.000000001 | 0.154991081306871+170.490189437558i | 9999999999+9999999i | 0.154991082306871+170.490189437558i | -154990900.971672+1704903444115.76i | 9999999999.15499+10000169.4901894i | 0.154993988986746+170.490189429367i | 0.155093988986746+139.365162283287i | 11 | 139.3652
[34 empty] | 11.2 | 0.0001-30.5692230898998i | 0.000000001 | 0.154991081306871+173.590011063695i | 9999999999+9999999i | 0.154991082306871+173.590011063695i | -185989114.13322+1735901660374.03i | 9999999999.15499+10000172.5900111i | 0.15499409564527+173.590011055301i | 0.15509409564527+143.020787965401i | 11.2 | 143.0209
[34 empty] | 11.4 | 0.0001-30.0329209304279i | 0.000000001 | 0.154991081306871+176.689832689833i | 9999999999+9999999i | 0.154991082306871+176.689832689833i | -216987327.294778+1766899876632.31i | 9999999999.15499+10000175.6898327i | 0.154994204225568+176.689832681234i | 0.155094204225568+146.656911750806i | 11.4 | 146.657
[34 empty] | 11.6 | 0.0001-29.5151119488688i | 0.000000001 | 0.154991081306871+179.78965431597i | 9999999999+9999999i | 0.154991082306871+179.78965431597i | -247985540.456327+1797898092890.58i | 9999999999.15499+10000178.7896543i | 0.154994314727643+179.789654307165i | 0.155094314727643+150.274542358296i | 11.6 | 150.2746
[34 empty] | 11.8 | 0.0001-29.0148558141422i | 0.000000001 | 0.154991081306871+182.889475942107i | 9999999999+9999999i | 0.154991082306871+182.889475942107i | -278983753.617875+1828896309148.85i | 9999999999.15499+10000181.8894759i | 0.154994427151495+182.889475933093i | 0.155094427151495+153.874620118951i | 11.8 | 153.8747
[34 empty] | 12 | 0.0001-28.5312748839065i | 0.000000001 | 0.154991081306871+185.989297568245i | 9999999999+9999999i | 0.154991082306871+185.989297568245i | -309981966.779433+1859894525407.13i | 9999999999.15499+10000184.9892976i | 0.154994541497126+185.989297559021i | 0.155094541497126+157.458022675115i | 12 | 157.4581
[34 empty] | 12.2 | 0.0001-28.0635490661375i | 0.000000001 | 0.154991081306871+189.089119194382i | 9999999999+9999999i | 0.154991082306871+189.089119194382i | -340980179.940982+1890892741665.4i | 9999999999.15499+10000188.0891192i | 0.154994657764532+189.089119184945i | 0.155094657764532+161.025570118807i | 12.2 | 161.0256
Northeast Power Systems, Inc. | [33 empty] | 12.4 | 0.0001-27.610911177974i | 0.000000001 | 0.154991081306871+192.18894082052i | 9999999999+9999999i | 0.154991082306871+192.18894082052i | -371978393.10254+1921890957923.68i | 9999999999.15499+10000191.1889408i | 0.154994775953715+192.188940810869i | 0.155094775953715+164.578029632895i | 12.4 | 164.5781
Notch Filter Design - Stage/Branch: Branch/Stage #, Tuning Point: 4.70, Reference: Enter Job Name | [9 empty] | Page 2 | [23 empty] | 12.6 | 0.0001-27.1726427465776i | 0.000000001 | 0.154991081306871+195.288762446657i | 9999999999+9999999i | 0.154991082306871+195.288762446657i | -402976606.264088+1952889174181.95i | 9999999999.15499+10000194.2887624i | 0.154994896064675+195.28876243679i | 0.155094896064675+168.116119690212i | 12.6 | 168.1162
[34 empty] | 12.8 | 0.0001-26.7480702036623i | 0.000000001 | 0.154991081306871+198.388584072794i | 9999999999+9999999i | 0.154991082306871+198.388584072794i | -433974819.425637+1983887390440.22i | 9999999999.15499+10000197.3885841i | 0.154995018097413+198.388584062709i | 0.155095018097413+171.640513859047i | 12.8 | 171.6406
[34 empty] | 13 | 0.0001-26.3365614312983i | 0.000000001 | 0.154991081306871+201.488405698932i | 9999999999+9999999i | 0.154991082306871+201.488405698932i | -464973032.587195+2014885606698.5i | 9999999999.15499+10000200.4884057i | 0.154995142051927+201.488405688626i | 0.155095142051927+175.151844257328i | 13 | 175.1519
[34 empty] | 13.2 | 0.0001-25.9375226217332i | 0.000000001 | 0.154991081306871+204.588227325069i | 9999999999+9999999i | 0.154991082306871+204.588227325069i | -495971245.748744+2045883822956.77i | 9999999999.15499+10000203.5882273i | 0.154995267928217+204.588227314542i | 0.155095267928217+178.650704692809i | 13.2 | 178.6508
[34 empty] | 13.4 | 0.0001-25.5503954184237i | 0.000000001 | 0.154991081306871+207.688048951207i | 9999999999+9999999i | 0.154991082306871+207.688048951207i | -526969458.910302+2076882039215.05i | 9999999999.15499+10000206.688049i | 0.154995395726286+207.688048940456i | 0.155095395726286+182.137653522032i | 13.4 | 182.1377
[34 empty] | 13.6 | 0.0001-25.1746543093293i | 0.000000001 | 0.154991081306871+210.787870577344i | 9999999999+9999999i | 0.154991082306871+210.787870577344i | -557967672.071851+2107880255473.32i | 9999999999.15499+10000209.7878706i | 0.15499552544613+210.787870566367i | 0.15509552544613+185.613216257038i | 13.6 | 185.6133
[34 empty] | 13.8 | 0.0001-24.8098042468752i | 0.000000001 | 0.154991081306871+213.887692203481i | 9999999999+9999999i | 0.154991082306871+213.887692203481i | -588965885.233399+2138878471731.59i | 9999999999.15499+10000212.8876922i | 0.154995657087751+213.887692192276i | 0.155095657087751+189.077887945401i | 13.8 | 189.078
[34 empty] | 14 | 0.0001-24.4553784719199i | 0.000000001 | 0.154991081306871+216.987513829619i | 9999999999+9999999i | 0.154991082306871+216.987513829619i | -619964098.394957+2169876687989.87i | 9999999999.15499+10000215.9875138i | 0.154995790651149+216.987513818184i | 0.155095790651149+192.532135346264i | 14 | 192.5322
|  | SPECIFIED HARMONICS | [31 empty] | 14.2 | 0.0001-24.1109365216111i | 0.000000001 | 0.154991081306871+220.087335455756i | 9999999999+9999999i | 0.154991082306871+220.087335455756i | -650962311.556505+2200874904248.14i | 9999999999.15499+10000219.0873355i | 0.154995926136327+220.08733544409i | 0.155095926136327+195.976398922479i | 14.2 | 195.9765
Harmonic #: (n) |  | 1 | 3 | 5 | 7 | 11 | 13 | 17 | 19 | [24 empty] | 14.4 | 0.0001-23.7760624032554i | 0.000000001 | 0.154991081306871+223.187157081894i | 9999999999+9999999i | 0.154991082306871+223.187157081894i | -681960524.718064+2231873120506.42i | 9999999999.15499+10000222.1871571i | 0.154996063543278+223.187157069994i | 0.155096063543278+199.411094666739i | 14.4 | 199.4112
Filter Current (amps) (In) |  | 46.331 | 0 | 98 | 0 | 0 | 0 | 0 | 0 | [24 empty] | 14.6 | 0.0001-23.4503629182793i | 0.000000001 | 0.154991081306871+226.286978708031i | 9999999999+9999999i | 0.154991082306871+226.286978708031i | -712958737.879612+2262871336764.69i | 9999999999.15499+10000225.2869787i | 0.154996202872007+226.286978695896i | 0.155096202872007+202.836615777617i | 14.6 | 202.8367
VCAP HARMONIC VOLTAGE (volts) |  | 15862.5982 | 0 | 6710.5559 | 0 | 0 | 0 | 0 | 0 | [24 empty] | 14.8 | 0.0001-23.1334661220864i | 0.000000001 | 0.154991081306871+229.386800334168i | 9999999999+9999999i | 0.154991082306871+229.386800334168i | -743956951.041161+2293869553022.96i | 9999999999.15499+10000228.3868003i | 0.154996344122512+229.386800321795i | 0.155096344122512+206.253334199709i | 14.8 | 206.2534
IREACTOR CURRENT (amps) |  | 46.331 | 0 | 98 | 0 | 0 | 0 | 0 | 0 | [24 empty] | 15 | 0.0001-22.8250199071252i | 0.000000001 | 0.154991081306871+232.486621960306i | 9999999999+9999999i | 0.154991082306871+232.486621960306i | -774955164.202719+2324867769281.24i | 9999999999.15499+10000231.486622i | 0.154996487294797+232.486621947694i | 0.155096487294797+209.661602040569i | 15 | 209.6617
Filter Voltage Distortion |  | 100.1% | 0% | 5.845% | 0% | 0% | 0% | 0% | 0% | [24 empty] | 15.2 | 0.0001-22.5246906978209i | 0.000000001 | 0.154991081306871+235.586443586443i | 9999999999+9999999i | 0.154991082306871+235.586443586443i | -805953377.364268+2355865985539.51i | 9999999999.15499+10000234.5864436i | 0.154996632388856+235.58644357359i | 0.155096632388856+213.061752875769i | 15.2 | 213.0618
|  | SPECIFIED HARMONICS 1: SPECIFIED HARMONICS | [24 empty] | 15.4 | 0.0001-22.2321622471999i | 0.000000001 | 0.154991081306871+238.686265212581i | 9999999999+9999999i | 0.154991082306871+238.686265212581i | -836951590.525826+2386864201797.79i | 9999999999.15499+10000237.6862652i | 0.154996779404693+238.686265199485i | 0.155096779404693+216.454102952285i | 15.4 | 216.4542
Harmonic #: (n) |  | 23 | 25 | 29 | 31 | 35 | 37 | 41 | 43 | [5 empty] | 1 | 3 | 5 | 7 | 11 | 13 | 17 | 19 | [11 empty] | 15.6 | 0.0001-21.9471345260819i | 0.000000001 | 0.154991081306871+241.786086838718i | 9999999999+9999999i | 0.154991082306871+241.786086838718i | -867949803.687374+2417862418056.06i | 9999999999.15499+10000240.7860868i | 0.154996928342306+241.786086825377i | 0.155096928342306+219.838952299295i | 15.6 | 219.839
Filter Current (amps) (In) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | VCAP HARMONIC VOLTAGE (volts)^2 | 251622022.3974 | 0 | 45031559.8521 | 0 | 0 | 0 | 0 | 0 | [11 empty] | 15.8 | 0.0001-21.6693226966378i | 0.000000001 | 0.154991081306871+244.885908464855i | 9999999999+9999999i | 0.154991082306871+244.885908464855i | -898948016.848922+2448860634314.33i | 9999999999.15499+10000243.8859085i | 0.154997079201698+244.885908451267i | 0.155097079201698+223.216585754629i | 15.8 | 223.2166
VCAP HARMONIC VOLTAGE (volts) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | Filter Current (amps) (In)^2 | 2146.5638 | 0 | 9604 | 0 | 0 | 0 | 0 | 0 | [11 empty] | 16 | 0.0001-21.3984561629299i | 0.000000001 | 0.154991081306871+247.985730090993i | 9999999999+9999999i | 0.154991082306871+247.985730090993i | -929946230.010481+2479858850572.61i | 9999999999.15499+10000246.9857301i | 0.154997231982865+247.985730077156i | 0.155097231982865+226.587273914226i | 16 | 226.5873
IREACTOR CURRENT (amps) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | kvar (single phase) | 734.9304 | 0 | 657.6345 | 0 | 0 | 0 | 0 | 0 | [11 empty] | 16.2 | 0.0001-21.1342776917826i | 0.000000001 | 0.154991081306871+251.08555171713i | 9999999999+9999999i | 0.154991082306871+251.08555171713i | -960944443.172029+2510857066830.88i | 9999999999.15499+10000250.0855517i | 0.154997386685809+251.085551703042i | 0.155097386685809+229.951274011259i | 16.2 | 229.9513
Filter Voltage Distortion | [33 empty] | 16.4 | 0.0001-20.8765425979804i | 0.000000001 | 0.154991081306871+254.185373343268i | 9999999999+9999999i | 0.154991082306871+254.185373343268i | -991942656.333588+2541855283089.16i | 9999999999.15499+10000253.1853733i | 0.154997543310529+254.185373328927i | 0.155097543310529+233.308830730947i | 16.4 | 233.3089 | bar: SPECIFIED HARMONICS 1 to SPECIFIED HARMONICS 19
System Voltage Distortion (Vthd %) |  | SPECIFIED HARMONICS 1: 5.845% | [24 empty] | 16.6 | 0.0001-20.6250179883661i | 0.000000001 | 0.154991081306871+257.285194969405i | 9999999999+9999999i | 0.154991082306871+257.285194969405i | -1022940869.49514+2572853499347.43i | 9999999999.15499+10000256.285195i | 0.154997701857029+257.28519495481i | 0.155097701857029+236.660176966444i | 16.6 | 236.6602
[15 empty] | 23 | 25 | 29 | 31 | 35 | 37 | 41 | 43 | [11 empty] | 16.8 | 0.0001-20.3794820599332i | 0.000000001 | 0.154991081306871+260.385016595542i | 9999999999+9999999i | 0.154991082306871+260.385016595542i | -1053939082.65668+2603851715605.7i | 9999999999.15499+10000259.3850166i | 0.154997862325304+260.38501658069i | 0.155097862325304+240.005534520757i | 16.8 | 240.0056
FILTER ONE-LINE DIAGRAM | [13 empty] | VCAP HARMONIC VOLTAGE (volts)^2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [11 empty] | 17 | 0.0001-20.1397234474634i | 0.000000001 | 0.154991081306871+263.48483822168i | 9999999999+9999999i | 0.154991082306871+263.48483822168i | -1084937295.81824+2634849931863.98i | 9999999999.15499+10000262.4848382i | 0.154998024715356+263.48483820657i | 0.155098024715356+243.345114759107i | 17 | 243.3452
|  | SPECIFIED HARMONICS 17: Reactor Fundamental Design Margin:; SPECIFIED HARMONICS 19: 1.5 |  |  |  |  | Filter Current (amps) (In)^2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [11 empty] | 17.2 | 0.0001-19.905540616679i | 0.000000001 | 0.154991081306871+266.584659847817i | 9999999999+9999999i | 0.154991082306871+266.584659847817i | -1115935508.97979+2665848148122.25i | 9999999999.15499+10000265.5846598i | 0.154998189027184+266.584659832446i | 0.155098189027184+246.679119215767i | 17.2 | 246.6792
Filter Bank Fundamental amps 46.3 amps/phase |  | SPECIFIED HARMONICS 17: Reactor Harmonic Design Margin:; SPECIFIED HARMONICS 19: 1.5 |  |  |  |  | kvar (single phase) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [11 empty] | 17.4 | 0.0001-19.6767412992459i | 0.000000001 | 0.154991081306871+269.684481473955i | 9999999999+9999999i | 0.154991082306871+269.684481473955i | -1146933722.14135+2696846364380.53i | 9999999999.15499+10000268.6844815i | 0.154998355260791+269.684481458322i | 0.155098355260791+250.007740159076i | 17.4 | 250.0078
Specified Filter Bank RMS AMPS 108.4 amps/phase | [33 empty] | 17.6 | 0.0001-19.4531419662999i | 0.000000001 | 0.154991081306871+272.784303100092i | 9999999999+9999999i | 0.154991082306871+272.784303100092i | -1177931935.3029+2727844580638.8i | 9999999999.15499+10000271.7843031i | 0.154998523416173+272.784303084195i | 0.155098523416173+253.331161117895i | 17.6 | 253.3312
|  | SPECIFIED HARMONICS 11: Reference: Notch Filter Design - Stage/Branch: Branch/Stage #, Tuning Point: 4.70, Reference: Enter Job Name | [24 empty] | 17.8 | 0.0001-19.2345673374651i | 0.000000001 | 0.154991081306871+275.884124726229i | 9999999999+9999999i | 0.154991082306871+275.884124726229i | -1208930148.46445+2758842796897.07i | 9999999999.15499+10000274.8841247i | 0.154998693493332+275.884124710065i | 0.155098693493332+256.6495573726i | 17.8 | 256.6496
[34 empty] | 18 | 0.0001-19.0208499226043i | 0.000000001 | 0.154991081306871+278.983946352367i | 9999999999+9999999i | 0.154991082306871+278.983946352367i | -1239928361.626+2789841013155.35i | 9999999999.15499+10000277.9839464i | 0.154998865492271+278.983946335935i | 0.155098865492271+259.963096413331i | 18 | 259.9631 | bar: SPECIFIED HARMONICS 11 to SPECIFIED HARMONICS 19
Iron-Core Filter Reactor: 15.5 ohms, 41.11 mH |  | SPECIFIED HARMONICS 11: Current Ratings; SPECIFIED HARMONICS 19: Design & Construction Details | [24 empty] | 18.2 | 0.0001-18.8118295937845i | 0.000000001 | 0.154991081306871+282.083767978504i | 9999999999+9999999i | 0.154991082306871+282.083767978504i | -1270926574.78755+2820839229413.62i | 9999999999.15499+10000281.083768i | 0.154999039412984+282.083767961802i | 0.155099039412984+263.271938368017i | 18.2 | 263.272
I1= 46.3 amps nominal |  | SPECIFIED HARMONICS 11: Harm #; SPECIFIED HARMONICS 13: Amps; SPECIFIED HARMONICS 19: Quantity: | 3 |  |  |  | harmonic # | 1 | 3 | 5 | 7 | 11 | 13 | 17 | 19 | 23 | 25 | 29 | 31 | 35 | 37 | 41 | 43 |  |  |  | 18.4 | 0.0001-18.6073531851564i | 0.000000001 | 0.154991081306871+285.183589604642i | 9999999999+9999999i | 0.154991082306871+285.183589604642i | -1301924787.94911+2851837445671.9i | 9999999999.15499+10000284.1835896i | 0.154999215255473+285.183589587668i | 0.155099215255473+266.576236402512i | 18.4 | 266.5763
|  | SPECIFIED HARMONICS 11: 1; SPECIFIED HARMONICS 13: 69.4965; SPECIFIED HARMONICS 19: Number of Phases: | 3 |  |  |  | Total filter amps | 46.331 | 0 | 98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 18.6 | 0.0001-18.4072741186494i | 0.000000001 | 0.154991081306871+288.283411230779i | 9999999999+9999999i | 0.154991082306871+288.283411230779i | -1332923001.11066+2882835661930.17i | 9999999999.15499+10000287.2834112i | 0.15499939301974+288.283411213531i | 0.15509939301974+269.876137094882i | 18.6 | 269.8762 |  | 69.4965 | 4829.7685
|  | SPECIFIED HARMONICS 11: 3; SPECIFIED HARMONICS 13: 0; SPECIFIED HARMONICS 19: System Voltage (kV): | 26.2 kV |  |  |  | R & X EQUIVALENT IMPEDANCE | 15.4991 | 46.4973 | 77.4955 | 108.4938 | 170.4902 | 201.4884 | 263.4848 | 294.4831 | 356.4795 | 387.4777 | 449.4741 | 480.4724 | 542.4688 | 573.467 | 635.4634 | 666.4616 |  |  |  | 18.8 | 0.0001-18.2114520535573i | 0.000000001 | 0.154991081306871+291.383232856916i | 9999999999+9999999i | 0.154991082306871+291.383232856916i | -1363921214.27221+2913833878188.44i | 9999999999.15499+10000290.3832329i | 0.154999572705786+291.383232839393i | 0.155099572705786+273.171780785836i | 18.8 | 273.1718 |  | 0 | 0
|  | SPECIFIED HARMONICS 11: 5; SPECIFIED HARMONICS 13: 147; SPECIFIED HARMONICS 19: BIL Rating (kV): | 95 |  |  |  | I REACTOR | 46.331 | 0 | 98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 19 | 0.0001-18.0197525582567i | 0.000000001 | 0.154991081306871+294.483054483054i | 9999999999+9999999i | 0.154991082306871+294.483054483054i | -1394919427.43377+2944832094446.72i | 9999999999.15499+10000293.4830545i | 0.154999754313606+294.483054465253i | 0.155099754313606+276.463301906996i | 19 | 276.4633 |  | 147 | 21609
|  | SPECIFIED HARMONICS 11: 7; SPECIFIED HARMONICS 13: 0; SPECIFIED HARMONICS 19: Fundamental Frequency: | 60 | [23 empty] | 19.2 | 0.0001-17.8320468024416i | 0.000000001 | 0.154991081306871+297.582876109191i | 9999999999+9999999i | 0.154991082306871+297.582876109191i | -1425917640.59531+2975830310704.99i | 9999999999.15499+10000296.5828761i | 0.154999937843204+297.58287609111i | 0.155099937843204+279.750829288668i | 19.2 | 279.7509 |  | 0 | 0
|  | SPECIFIED HARMONICS 11: 11; SPECIFIED HARMONICS 13: 0; SPECIFIED HARMONICS 19: Inductance (mH): | 41.1139 | [23 empty] | 19.4 | 0.0001-17.6482112683958i | 0.000000001 | 0.154991081306871+300.682697735329i | 9999999999+9999999i | 0.154991082306871+300.682697735329i | -1456915853.75687+3006828526963.27i | 9999999999.15499+10000299.6826977i | 0.155000123294578+300.682697716967i | 0.155100123294578+283.034486448571i | 19.4 | 283.0345 |  | 0 | 0
|  | SPECIFIED HARMONICS 11: 13; SPECIFIED HARMONICS 13: 0; SPECIFIED HARMONICS 19: Reactance at 60Hz (ohms): | 15.4991 | [23 empty] | 19.6 | 0.0001-17.4681274799428i | 0.000000001 | 0.154991081306871+303.782519361466i | 9999999999+9999999i | 0.154991082306871+303.782519361466i | -1487914066.91842+3037826743221.55i | 9999999999.15499+10000302.7825194i | 0.155000310667732+303.782519342821i | 0.155100310667732+286.314391862878i | 19.6 | 286.3144 |  | 0 | 0
Main Capacitor Fuse: 42 (Minimum Amps) |  | SPECIFIED HARMONICS 11: 17; SPECIFIED HARMONICS 13: 0; SPECIFIED HARMONICS 19: Taps: | None |  |  |  | Total filter amps^2 | 2146.5638 | 0 | 9604 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Total Filter RMS Amps | 108.4 |  | 19.8 | 0.0001-17.2916817478221i | 0.000000001 | 0.154991081306871+306.882340987603i | 9999999999+9999999i | 0.154991082306871+306.882340987603i | -1518912280.07997+3068824959479.82i | 9999999999.15499+10000305.882341i | 0.15500049996266+306.882340968673i | 0.15510049996266+289.590659220851i | 19.8 | 289.5907 |  | 0 | 0
|  | SPECIFIED HARMONICS 11: 19; SPECIFIED HARMONICS 13: 0; SPECIFIED HARMONICS 19: Insulation Type: | Nomex |  |  |  | I2R REACTOR LOSSES | 332.6982 | 0 | 1488.5343 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 20 | 0.0001-17.1187649303439i | 0.000000001 | 0.154991081306871+309.982162613741i | 9999999999+9999999i | 0.154991082306871+309.982162613741i | -1549910493.24153+3099823175738.1i | 9999999999.15499+10000308.9821626i | 0.155000691179365+309.982162594523i | 0.155100691179365+292.863397664179i | 20 | 292.8634 |  | 0 | 0
|  | SPECIFIED HARMONICS 11: 23; SPECIFIED HARMONICS 13: 0; SPECIFIED HARMONICS 19: Ambient: | 60C | [23 empty] | 20.2 | 0.0001-16.9492722082613i | 0.000000001 | 0.154991081306871+313.081984239878i | 9999999999+9999999i | 0.154991082306871+313.081984239878i | -1580908706.40308+3130821391996.37i | 9999999999.15499+10000312.0819842i | 0.155000884317846+313.081984220371i | 0.155100884317846+296.13271201211i | 20.2 | 296.1328 |  | 0 | 0
|  | SPECIFIED HARMONICS 11: 25; SPECIFIED HARMONICS 13: 0; SPECIFIED HARMONICS 19: Temperature Rise: | 115C Rise over Ambient | [23 empty] | 20.4 | 0.0001-16.7831028728862i | 0.000000001 | 0.154991081306871+316.181805866016i | 9999999999+9999999i | 0.154991082306871+316.181805866016i | -1611906919.56464+3161819608254.65i | 9999999999.15499+10000315.1818059i | 0.155001079378108+316.181805846218i | 0.155101079378108+299.398702973332i | 20.4 | 299.3987 |  | 0 | 0
Main Capacitor: Qty(6), 422 kvar, 17 kV, 3.87 µF/Can |  | SPECIFIED HARMONICS 11: 29; SPECIFIED HARMONICS 13: 0; SPECIFIED HARMONICS 19: Winding Type: | CU/AL - Based On Price | [23 empty] | 20.6 | 0.0001-16.6201601265475i | 0.000000001 | 0.154991081306871+319.281627492153i | 9999999999+9999999i | 0.154991082306871+319.281627492153i | -1642905132.72618+3192817824512.92i | 9999999999.15499+10000318.2816275i | 0.155001276360144+319.281627472062i | 0.155101276360144+302.661467345514i | 20.6 | 302.6615 |  | 0 | 0
|  | SPECIFIED HARMONICS 11: 31; SPECIFIED HARMONICS 13: 0; SPECIFIED HARMONICS 19: Tack Winding to Core: | Yes | [23 empty] | 20.8 | 0.0001-16.4603508945615i | 0.000000001 | 0.154991081306871+322.38144911829i | 9999999999+9999999i | 0.154991082306871+322.38144911829i | -1673903345.88773+3223816040771.19i | 9999999999.15499+10000321.3814491i | 0.155001475263956+322.381449097904i | 0.155101475263956+305.921098203343i | 20.8 | 305.9211 |  | 0 | 0
|  | SPECIFIED HARMONICS 11: 35; SPECIFIED HARMONICS 13: 0; SPECIFIED HARMONICS 19: Enclosure: | None/Open Construction | [23 empty] | 21 | 0.0001-16.3035856479466i | 0.000000001 | 0.154991081306871+325.481270744428i | 9999999999+9999999i | 0.154991082306871+325.481270744428i | -1704901559.04929+3254814257029.47i | 9999999999.15499+10000324.4812707i | 0.155001676089545+325.481270723745i | 0.155101676089545+309.177685075798i | 21 | 309.1777 |  | 0 | 0
26.2kV, 60Hz Notch-Filter, Wye-Connected |  | SPECIFIED HARMONICS 11: 37; SPECIFIED HARMONICS 13: 0 | [24 empty] | 21.2 | 0.0001-16.1497782361735i | 0.000000001 | 0.154991081306871+328.581092370565i | 9999999999+9999999i | 0.154991082306871+328.581092370565i | -1735899772.21084+3285812473287.74i | 9999999999.15499+10000327.5810924i | 0.155001878836914+328.581092349583i | 0.155101878836914+312.431314113409i | 21.2 | 312.4314 |  | 0 | 0
2.10 MVAR 3-Phase, 4.7 Tuning |  | SPECIFIED HARMONICS 11: 41; SPECIFIED HARMONICS 13: 0 | [24 empty] | 21.4 | 0.0001-15.9988457292934i | 0.000000001 | 0.154991081306871+331.680913996703i | 9999999999+9999999i | 0.154991082306871+331.680913996703i | -1766897985.3724+3316810689546.02i | 9999999999.15499+10000330.680914i | 0.155002083506057+331.68091397542i | 0.155102083506057+315.682068246127i | 21.4 | 315.6821 |  | 0 | 0
|  | SPECIFIED HARMONICS 11: 43; SPECIFIED HARMONICS 13: 0 | [24 empty] | 21.6 | 0.0001-15.850708268837i | 0.000000001 | 0.154991081306871+334.78073562284i | 9999999999+9999999i | 0.154991082306871+334.78073562284i | -1797896198.53395+3347808905804.29i | 9999999999.15499+10000333.7807356i | 0.155002290096977+334.780735601255i | 0.155102290096977+318.930027332418i | 21.6 | 318.9301 |  | 0 | 0
|  | SPECIFIED HARMONICS 11: RMS:; SPECIFIED HARMONICS 13: 162.6 | [24 empty] | 21.8 | 0.0001-15.705288926921i | 0.000000001 | 0.154991081306871+337.880557248977i | 9999999999+9999999i | 0.154991082306871+337.880557248977i | -1828894411.69549+3378807122062.56i | 9999999999.15499+10000336.8805572i | 0.155002498609674+337.880557227087i | 0.155102498609674+322.175268300166i | 21.8 | 322.1753 |  |  | 26438.7685
[34 empty] | 22 | 0.0001-15.5625135730399i | 0.000000001 | 0.154991081306871+340.980378875115i | 9999999999+9999999i | 0.154991082306871+340.980378875115i | -1859892624.85705+3409805338320.84i | 9999999999.15499+10000339.9803789i | 0.155002709044151+340.980378852918i | 0.155102709044151+325.417865279878i | 22 | 325.4179 |  |  | 162.6 | reactor RMS amps (for supplier with margin)
Where: | [33 empty] | 22.2 | 0.0001-15.4223107480576i | 0.000000001 | 0.154991081306871+344.080200501252i | 9999999999+9999999i | 0.154991082306871+344.080200501252i | -1890890838.0186+3440803554579.11i | 9999999999.15499+10000343.0802005i | 0.155002921400402+344.080200478747i | 0.155102921400402+328.657889730689i | 22.2 | 328.6579
Xeff | Effective reactance of the harmonic filter | [32 empty] | 22.4 | 0.0001-15.2846115449499i | 0.000000001 | 0.154991081306871+347.18002212739i | 9999999999+9999999i | 0.154991082306871+347.18002212739i | -1921889051.18016+3471801770837.39i | 9999999999.15499+10000346.1800221i | 0.155003135678429+347.180022104575i | 0.155103135678429+331.895410559625i | 22.4 | 331.8954
Qeff | Effective Reactive Power (MVAR) of the harmonic filter (fundamental current only, not including harmonics) | [32 empty] | 22.6 | 0.0001-15.1493494958796i | 0.000000001 | 0.154991081306871+350.279843753527i | 9999999999+9999999i | 0.154991082306871+350.279843753527i | -1952887264.34171+3502799987095.66i | 9999999999.15499+10000349.2798438i | 0.155003351878237+350.279843730399i | 0.155103351878237+335.130494234519i | 22.6 | 335.1305
QFILTER | Kvar rating of harmonic filter. Includes reactive power associated with fundamental and harmonic current. | [32 empty] | 22.8 | 0.0001-15.016460465214i | 0.000000001 | 0.154991081306871+353.379665379665i | 9999999999+9999999i | 0.154991082306871+353.379665379665i | -1983885477.50327+3533798203353.94i | 9999999999.15499+10000352.3796654i | 0.155003569999818+353.379665356223i | 0.155103569999818+338.363204891009i | 22.8 | 338.3632
QRATED PER PHASE | kvar rating of capacitors at their rated voltage (not the application voltage) | [32 empty] | 23 | 0.0001-14.8858825481251i | 0.000000001 | 0.154991081306871+356.479487005802i | 9999999999+9999999i | 0.154991082306871+356.479487005802i | -2014883690.66481+3564796419612.21i | 9999999999.15499+10000355.479487i | 0.155003790043177+356.479486982044i | 0.155103790043177+341.593604433919i | 23 | 341.5936
VLLSYS | Nominal System Line-to-Line Voltage | [32 empty] | 23.2 | 0.0001-14.7575559744344i | 0.000000001 | 0.154991081306871+359.579308631939i | 9999999999+9999999i | 0.154991082306871+359.579308631939i | -2045881903.82636+3595794635870.48i | 9999999999.15499+10000358.5793086i | 0.155004012008311+359.579308607863i | 0.155104012008311+344.821752633429i | 23.2 | 344.8218
XC | Capacitive reactance of the harmonic filter capacitor at fundamental frequency | [32 empty] | 23.4 | 0.0001-14.631423017388i | 0.000000001 | 0.154991081306871+362.679130258077i | 9999999999+9999999i | 0.154991082306871+362.679130258077i | -2076880116.98792+3626792852128.76i | 9999999999.15499+10000361.6791303i | 0.155004235895227+362.679130233681i | 0.155104235895227+348.047707216293i | 23.4 | 348.0477
XL | Inductive Reactance of the harmonic filter reactor at fundamental frequency | [32 empty] | 23.6 | 0.0001-14.5074279070711i | 0.000000001 | 0.154991081306871+365.778951884214i | 9999999999+9999999i | 0.154991082306871+365.778951884214i | -2107878330.14947+3657791068387.03i | 9999999999.15499+10000364.7789519i | 0.155004461703915+365.778951859496i | 0.155104461703915+351.271523952425i | 23.6 | 351.2716
h | harmonic number of tuning filter tuning point | [32 empty] | 23.8 | 0.0001-14.3855167481882i | 0.000000001 | 0.154991081306871+368.878773510352i | 9999999999+9999999i | 0.154991082306871+368.878773510352i | -2138876543.31103+3688789284645.31i | 9999999999.15499+10000367.8787735i | 0.155004689434381+368.87877348531i | 0.155104689434381+354.493256737122i | 23.8 | 354.4933
f | frequency | [32 empty] | 24 | 0.0001-14.2656374419533i | 0.000000001 | 0.154991081306871+371.978595136489i | 9999999999+9999999i | 0.154991082306871+371.978595136489i | -2169874756.47258+3719787500903.58i | 9999999999.15499+10000370.9785951i | 0.155004919086623+371.978595111121i | 0.155104919086623+357.712957669168i | 24 | 357.713
H | Reactor Henry Rating (milliHenrys) | [32 empty] | 24.2 | 0.0001-14.1477396118545i | 0.000000001 | 0.154991081306871+375.078416762626i | 9999999999+9999999i | 0.154991082306871+375.078416762626i | -2200872969.63412+3750785717161.85i | 9999999999.15499+10000374.0784168i | 0.155005150660647+375.078416736931i | 0.155105150660647+360.930677125076i | 24.2 | 360.9307
IRATED FUNDAMENTAL | Fundamental Current Rating of Filter Bank | [32 empty] | 24.4 | 0.0001-14.0317745330688i | 0.000000001 | 0.154991081306871+378.178238388764i | 9999999999+9999999i | 0.154991082306871+378.178238388764i | -2231871182.79568+3781783933420.13i | 9999999999.15499+10000377.1782384i | 0.155005384156444+378.178238362739i | 0.155105384156444+364.14646382967i | 24.4 | 364.1465
VCAP FUNDAMENTAL VOLTAGE | Fundamental Voltage Drop Across Capacitor | [32 empty] | 24.6 | 0.0001-13.9176950653203i | 0.000000001 | 0.154991081306871+381.278060014901i | 9999999999+9999999i | 0.154991082306871+381.278060014901i | -2262869395.95723+3812782149678.4i | 9999999999.15499+10000380.27806i | 0.155005619574017+381.278059988544i | 0.155105619574017+367.360364923224i | 24.6 | 367.3604
VCAP HARMONIC VOLTAGE | Harmonic Voltage Drop Across Capacitor | [32 empty] | 24.8 | 0.0001-13.805455588987i | 0.000000001 | 0.154991081306871+384.377881641039i | 9999999999+9999999i | 0.154991082306871+384.377881641039i | -2293867609.11879+3843780365936.68i | 9999999999.15499+10000383.3778816i | 0.155005856913367+384.377881614349i | 0.155105856913367+370.572426025362i | 24.8 | 370.5725
VCAP RMS VOLTAGE | Capacitor RMS Voltage (Fundamental Voltage + Harmonic Voltages) | [32 empty] | 25 | 0.0001-13.6950119442751i | 0.000000001 | 0.154991081306871+387.477703267176i | 9999999999+9999999i | 0.154991082306871+387.477703267176i | -2324865822.28034+3874778582194.95i | 9999999999.15499+10000386.4777033i | 0.155006096174497+387.47770324015i | 0.155106096174497+373.782691295875i | 25 | 373.7827
VPEAK CAP VOLTAGE | Capacitor Voltage assuming or harmonics are coincident | [32 empty] | 25.2 | 0.0001-13.5863213732888i | 0.000000001 | 0.154991081306871+390.577524893313i | 9999999999+9999999i | 0.154991082306871+390.577524893313i | -2355864035.44189+3905776798453.22i | 9999999999.15499+10000389.5775249i | 0.155006337357401+390.57752486595i | 0.155106337357401+376.991203492661i | 25.2 | 376.9912
N | Number of Capacitors per phase | [32 empty] | 25.4 | 0.0001-13.4793424648377i | 0.000000001 | 0.154991081306871+393.677346519451i | 9999999999+9999999i | 0.154991082306871+393.677346519451i | -2386862248.60345+3936775014711.5i | 9999999999.15499+10000392.6773465i | 0.155006580462082+393.677346491749i | 0.155106580462082+380.198004026911i | 25.4 | 380.198
VCAP var rating | Capacitor Can Var Rating (in Kvar) | [32 empty] | 25.6 | 0.0001-13.3740351018312i | 0.000000001 | 0.154991081306871+396.777168145588i | 9999999999+9999999i | 0.154991082306871+396.777168145588i | -2417860461.76499+3967773230969.77i | 9999999999.15499+10000395.7771681i | 0.155006825488541+396.777168117545i | 0.155106825488541+383.403133015714i | 25.6 | 383.4032
ICAP RMS CURRENT | RMS Current Seen By Capacitor (amps) | [32 empty] | 25.8 | 0.0001-13.2703604111193i | 0.000000001 | 0.154991081306871+399.876989771726i | 9999999999+9999999i | 0.154991082306871+399.876989771726i | -2448858674.92655+3998771447228.05i | 9999999999.15499+10000398.8769898i | 0.155007072436779+399.87698974334i | 0.155107072436779+386.606629332221i | 25.8 | 386.6067
IFILTER RMS CURRENT | RMS Current into Filter Branch (amps) | [32 empty] | 26 | 0.0001-13.1682807156492i | 0.000000001 | 0.154991081306871+402.976811397863i | 9999999999+9999999i | 0.154991082306871+402.976811397863i | -2479856888.0881+4029769663486.32i | 9999999999.15499+10000401.9768114i | 0.15500732130679+402.976811369132i | 0.15510732130679+389.808530653483i | 26 | 389.8086
DF | Damping Factor is defined as the resistance of the resistor to the reactance of the reactor at the filter tuned frequency | [32 empty] | 26.2 | 0.0001-13.0677594888121i | 0.000000001 | 0.154991081306871+406.076633024i | 9999999999+9999999i | 0.154991082306871+406.076633024i | -2510855101.24965+4060767879744.59i | 9999999999.15499+10000405.076633i | 0.155007572098578+406.076632994922i | 0.155107572098578+393.00887350611i | 26.2 | 393.0089
* Formulas taken From IEEE Std. 1531-2003 - IEEE Guide for Application and Specification of Harmonic Filters | [33 empty] | 26.4 | 0.0001-12.9687613108666i | 0.000000001 | 0.154991081306871+409.176454650138i | 9999999999+9999999i | 0.154991082306871+409.176454650138i | -2541853314.41121+4091766096002.87i | 9999999999.15499+10000408.1764547i | 0.155007824812148+409.176454620711i | 0.155107824812148+396.207693309844i | 26.4 | 396.2077
[34 empty] | 26.6 | 0.0001-12.8712518273263i | 0.000000001 | 0.154991081306871+412.276276276275i | 9999999999+9999999i | 0.154991082306871+412.276276276275i | -2572851527.57275+4122764312261.14i | 9999999999.15499+10000411.2762763i | 0.155008079447491+412.276276246497i | 0.155108079447491+399.405024419171i | 26.6 | 399.4051
[34 empty] | 26.8 | 0.0001-12.7751977092119i | 0.000000001 | 0.154991081306871+415.376097902413i | 9999999999+9999999i | 0.154991082306871+415.376097902413i | -2603849740.73431+4153762528519.42i | 9999999999.15499+10000414.3760979i | 0.15500833600461+415.376097872283i | 0.15510833600461+402.600900163071i | 26.8 | 402.6009
[34 empty] | 27 | 0.0001-12.6805666150696i | 0.000000001 | 0.154991081306871+418.47591952855i | 9999999999+9999999i | 0.154991082306871+418.47591952855i | -2634847953.89586+4184760744777.69i | 9999999999.15499+10000417.4759195i | 0.155008594483505+418.475919498065i | 0.155108594483505+405.795352882995i | 27 | 405.7954
[34 empty] | 27.2 | 0.0001-12.5873271546646i | 0.000000001 | 0.154991081306871+421.575741154687i | 9999999999+9999999i | 0.154991082306871+421.575741154687i | -2665846167.05741+4215758961035.96i | 9999999999.15499+10000420.5757412i | 0.155008854884182+421.575741123845i | 0.155108854884182+408.98841396918i | 27.2 | 408.9884
[34 empty] | 27.4 | 0.0001-12.4954488542656i | 0.000000001 | 0.154991081306871+424.675562780825i | 9999999999+9999999i | 0.154991082306871+424.675562780825i | -2696844380.21897+4246757177294.24i | 9999999999.15499+10000423.6755628i | 0.155009117206632+424.675562749625i | 0.155109117206632+412.180113895359i | 27.4 | 412.1801
Northeast Power Systems, Inc. | [33 empty] | 27.6 | 0.0001-12.4049021234376i | 0.000000001 | 0.154991081306871+427.775384406962i | 9999999999+9999999i | 0.154991082306871+427.775384406962i | -2727842593.38052+4277755393552.51i | 9999999999.15499+10000426.7753844i | 0.155009381450858+427.775384375402i | 0.155109381450858+415.370482251964i | 27.6 | 415.3705
Notch Filter Design - Stage/Branch: Branch/Stage #, Tuning Point: 4.70, Reference: Enter Job Name | [9 empty] | Page 3 | [23 empty] | 27.8 | 0.0001-12.315658223269i | 0.000000001 | 0.154991081306871+430.8752060331i | 9999999999+9999999i | 0.154991082306871+430.8752060331i | -2758840806.54208+4308753609810.79i | 9999999999.15499+10000429.875206i | 0.155009647616862+430.875206001177i | 0.155109647616862+418.559547777908i | 27.8 | 418.5596
[34 empty] | 28 | 0.0001-12.2276892359599i | 0.000000001 | 0.154991081306871+433.975027659237i | 9999999999+9999999i | 0.154991082306871+433.975027659237i | -2789839019.70362+4339751826069.06i | 9999999999.15499+10000432.9750277i | 0.155009915704648+433.97502762695i | 0.155109915704648+421.74733839099i | 28 | 421.7474
[34 empty] | 28.2 | 0.0001-12.1409680357049i | 0.000000001 | 0.154991081306871+437.074849285374i | 9999999999+9999999i | 0.154991082306871+437.074849285374i | -2820837232.86517+4370750042327.33i | 9999999999.15499+10000436.0748493i | 0.155010185714205+437.074849252721i | 0.155110185714205+424.933881217016i | 28.2 | 424.9339
[34 empty] | 28.4 | 0.0001-12.0554682608056i | 0.000000001 | 0.154991081306871+440.174670911512i | 9999999999+9999999i | 0.154991082306871+440.174670911512i | -2851835446.02673+4401748258585.61i | 9999999999.15499+10000439.1746709i | 0.155010457645539+440.174670878491i | 0.155110457645539+428.119202617685i | 28.4 | 428.1192
[34 empty] | 28.6 | 0.0001-11.9711642869538i | 0.000000001 | 0.154991081306871+443.274492537649i | 9999999999+9999999i | 0.154991082306871+443.274492537649i | -2882833659.18828+4432746474843.88i | 9999999999.15499+10000442.2744925i | 0.15501073149865+443.274492504258i | 0.15511073149865+431.303328217304i | 28.6 | 431.3034
[34 empty] | 28.8 | 0.0001-11.8880312016277i | 0.000000001 | 0.154991081306871+446.374314163787i | 9999999999+9999999i | 0.154991082306871+446.374314163787i | -2913831872.34984+4463744691102.16i | 9999999999.15499+10000445.3743142i | 0.155011007273542+446.374314130024i | 0.155111007273542+434.486282928396i | 28.8 | 434.4863
[34 empty] | 29 | 0.0001-11.8060447795475i | 0.000000001 | 0.154991081306871+449.474135789924i | 9999999999+9999999i | 0.154991082306871+449.474135789924i | -2944830085.51138+4494742907360.43i | 9999999999.15499+10000448.4741358i | 0.155011284970208+449.474135755787i | 0.155111284970208+437.66809097624i | 29 | 437.6681
[34 empty] | 29.2 | 0.0001-11.7251814591397i | 0.000000001 | 0.154991081306871+452.573957416061i | 9999999999+9999999i | 0.154991082306871+452.573957416061i | -2975828298.67293+4525741123618.7i | 9999999999.15499+10000451.5739574i | 0.155011564588649+452.573957381548i | 0.155111564588649+440.848775922408i | 29.2 | 440.8488
[34 empty] | 29.4 | 0.0001-11.6454183199618i | 0.000000001 | 0.154991081306871+455.673779042199i | 9999999999+9999999i | 0.154991082306871+455.673779042199i | -3006826511.83449+4556739339876.98i | 9999999999.15499+10000454.673779i | 0.155011846128868+455.673779007309i | 0.155111846128868+444.028360687347i | 29.4 | 444.0284
[34 empty] | 29.6 | 0.0001-11.5667330610432i | 0.000000001 | 0.154991081306871+458.773600668336i | 9999999999+9999999i | 0.154991082306871+458.773600668336i | -3037824724.99604+4587737556135.25i | 9999999999.15499+10000457.7736007i | 0.155012129590868+458.773600633066i | 0.155112129590868+447.206867572023i | 29.6 | 447.2069
[34 empty] | 29.8 | 0.0001-11.4891039800966i | 0.000000001 | 0.154991081306871+461.873422294474i | 9999999999+9999999i | 0.154991082306871+461.873422294474i | -3068822938.1576+4618735772393.53i | 9999999999.15499+10000460.8734223i | 0.15501241497464+461.873422258823i | 0.15511241497464+450.384318278726i | 29.8 | 450.3843
[34 empty] | 30 | 0.0001-11.4125099535626i | 0.000000001 | 0.154991081306871+464.973243920611i | 9999999999+9999999i | 0.154991082306871+464.973243920611i | -3099821151.31915+4649733988651.8i | 9999999999.15499+10000463.9732439i | 0.155012702280189+464.973243884576i | 0.155112702280189+453.560733931013i | 30 | 453.5608
[34 empty] | 30.2 | 0.0001-11.3369304174463i | 0.000000001 | 0.154991081306871+468.073065546748i | 9999999999+9999999i | 0.154991082306871+468.073065546748i | -3130819364.4807+4680732204910.08i | 9999999999.15499+10000467.0730655i | 0.155012991507516+468.073065510329i | 0.155112991507516+456.736135092883i | 30.2 | 456.7362
[34 empty] | 30.4 | 0.0001-11.2623453489105i | 0.000000001 | 0.154991081306871+471.172887172886i | 9999999999+9999999i | 0.154991082306871+471.172887172886i | -3161817577.64225+4711730421168.36i | 9999999999.15499+10000470.1728872i | 0.155013282656625+471.17288713608i | 0.155113282656625+459.91054178717i | 30.4 | 459.9106
[34 empty] | 30.6 | 0.0001-11.1887352485908i | 0.000000001 | 0.154991081306871+474.272708799023i | 9999999999+9999999i | 0.154991082306871+474.272708799023i | -3192815790.8038+4742728637426.63i | 9999999999.15499+10000473.2727088i | 0.155013575727505+474.272708761827i | 0.155113575727505+463.083973513236i | 30.6 | 463.084
[34 empty] | 30.8 | 0.0001-11.1160811235999i | 0.000000001 | 0.154991081306871+477.372530425161i | 9999999999+9999999i | 0.154991082306871+477.372530425161i | -3223814003.96536+4773726853684.91i | 9999999999.15499+10000476.3725304i | 0.155013870720162+477.372530387574i | 0.155113870720162+466.256449263974i | 30.8 | 466.2565
[34 empty] | 31 | 0.0001-11.0443644711896i | 0.000000001 | 0.154991081306871+480.472352051298i | 9999999999+9999999i | 0.154991082306871+480.472352051298i | -3254812217.12691+4804725069943.18i | 9999999999.15499+10000479.4723521i | 0.1550141676346+480.472352013318i | 0.1551141676346+469.427987542128i | 31 | 469.428
[34 empty] | 31.2 | 0.0001-10.973567263041i | 0.000000001 | 0.154991081306871+483.572173677435i | 9999999999+9999999i | 0.154991082306871+483.572173677435i | -3285810430.28846+4835723286201.45i | 9999999999.15499+10000482.5721737i | 0.155014466470811+483.57217363906i | 0.155114466470811+472.598606376019i | 31.2 | 472.5986
[34 empty] | 31.4 | 0.0001-10.9036719301554i | 0.000000001 | 0.154991081306871+486.671995303573i | 9999999999+9999999i | 0.154991082306871+486.671995303573i | -3316808643.45002+4866721502459.73i | 9999999999.15499+10000485.6719953i | 0.155014767228798+486.671995264801i | 0.155114767228798+475.768323334646i | 31.4 | 475.7683
[34 empty] | 31.6 | 0.0001-10.8346613483189i | 0.000000001 | 0.154991081306871+489.77181692971i | 9999999999+9999999i | 0.154991082306871+489.77181692971i | -3347806856.61156+4897719718718i | 9999999999.15499+10000488.7718169i | 0.155015069908563+489.77181689054i | 0.155115069908563+478.937155542221i | 31.6 | 478.9372
[34 empty] | 31.8 | 0.0001-10.7665188241157i | 0.000000001 | 0.154991081306871+492.871638555848i | 9999999999+9999999i | 0.154991082306871+492.871638555848i | -3378805069.77312+4928717934976.28i | 9999999999.15499+10000491.8716386i | 0.15501537451011+492.871638516277i | 0.15511537451011+482.105119692161i | 31.8 | 482.1051
[34 empty] | 32 | 0.0001-10.6992280814649i | 0.000000001 | 0.154991081306871+495.971460181985i | 9999999999+9999999i | 0.154991082306871+495.971460181985i | -3409803282.93467+4959716151234.55i | 9999999999.15499+10000494.9714602i | 0.155015681033428+495.971460142011i | 0.155115681033428+485.272232060546i | 32 | 485.2723
[34 empty] | 32.2 | 0.0001-10.6327732486608i | 0.000000001 | 0.154991081306871+499.071281808122i | 9999999999+9999999i | 0.154991082306871+499.071281808122i | -3440801496.09622+4990714367492.82i | 9999999999.15499+10000498.0712818i | 0.155015989478523+499.071281767744i | 0.155115989478523+488.438508519083i | 32.2 | 488.4385
[34 empty] | 32.4 | 0.0001-10.5671388458913i | 0.000000001 | 0.154991081306871+502.17110343426i | 9999999999+9999999i | 0.154991082306871+502.17110343426i | -3471799709.25778+5021712583751.1i | 9999999999.15499+10000501.1711034i | 0.155016299845394+502.171103393475i | 0.155116299845394+491.603964547584i | 32.4 | 491.604
[34 empty] | 32.6 | 0.0001-10.5023097732171i | 0.000000001 | 0.154991081306871+505.270925060397i | 9999999999+9999999i | 0.154991082306871+505.270925060397i | -3502797922.41933+5052710800009.37i | 9999999999.15499+10000504.2709251i | 0.155016612134048+505.270925019204i | 0.155116612134048+494.768615245987i | 32.6 | 494.7686
[34 empty] | 32.8 | 0.0001-10.4382712989902i | 0.000000001 | 0.154991081306871+508.370746686535i | 9999999999+9999999i | 0.154991082306871+508.370746686535i | -3533796135.58088+5083709016267.65i | 9999999999.15499+10000507.3707467i | 0.155016926344475+508.370746644931i | 0.155116926344475+497.932475345941i | 32.8 | 497.9325
[34 empty] | 33 | 0.0001-10.3750090486933i | 0.000000001 | 0.154991081306871+511.470568312672i | 9999999999+9999999i | 0.154991082306871+511.470568312672i | -3564794348.74243+5114707232525.92i | 9999999999.15499+10000510.4705683i | 0.155017242476678+511.470568270656i | 0.155117242476678+501.095559221963i | 33 | 501.0956
[34 empty] | 33.2 | 0.0001-10.3125089941831i | 0.000000001 | 0.154991081306871+514.57038993881i | 9999999999+9999999i | 0.154991082306871+514.57038993881i | -3595792561.90399+5145705448784.2i | 9999999999.15499+10000513.5703899i | 0.155017560530657+514.57038989638i | 0.155117560530657+504.257880902197i | 33.2 | 504.2579
Filter Losses | [33 empty] | 33.4 | 0.0001-10.2507574433197i | 0.000000001 | 0.154991081306871+517.670211564947i | 9999999999+9999999i | 0.154991082306871+517.670211564947i | -3626790775.06554+5176703665042.47i | 9999999999.15499+10000516.6702116i | 0.155017880506419+517.670211522101i | 0.155117880506419+507.419454078781i | 33.4 | 507.4195
[34 empty] | 33.6 | 0.0001-10.1897410299666i | 0.000000001 | 0.154991081306871+520.770033191085i | 9999999999+9999999i | 0.154991082306871+520.770033191085i | -3657788988.2271+5207701881300.75i | 9999999999.15499+10000519.7700332i | 0.155018202403952+520.770033147821i | 0.155118202403952+510.580292117854i | 33.6 | 510.5803
Main Capacitor Losses |  | SPECIFIED HARMONICS 1: 126.6154; SPECIFIED HARMONICS 3: Watts, 3-Phase or 432 BTUs/Hour | [24 empty] | 33.8 | 0.0001-10.1294467043455i | 0.000000001 | 0.154991081306871+523.869854817222i | 9999999999+9999999i | 0.154991082306871+523.869854817222i | -3688787201.38865+5238700097559.02i | 9999999999.15499+10000522.8698548i | 0.155018526223262+523.869854773538i | 0.155118526223262+513.740408069193i | 33.8 | 513.7404
Main Capacitor Fuse Losses |  | SPECIFIED HARMONICS 1: 516.3376; SPECIFIED HARMONICS 3: Watts, 3-Phase or 1762 BTUs/Hour | [24 empty] | 34 | 0.0001-10.0698617237317i | 0.000000001 | 0.154991081306871+526.96967644336i | 9999999999+9999999i | 0.154991082306871+526.96967644336i | -3719785414.5502+5269698313817.3i | 9999999999.15499+10000525.9696764i | 0.15501885196435+526.969676399254i | 0.15511885196435+516.899814675522i | 34 | 516.8998
[34 empty] | 34.2 | 0.0001-10.010973643476i | 0.000000001 | 0.154991081306871+530.069498069497i | 9999999999+9999999i | 0.154991082306871+530.069498069497i | -3750783627.71175+5300696530075.57i | 9999999999.15499+10000529.0694981i | 0.155019179627219+530.069498024967i | 0.155119179627219+520.058524381491i | 34.2 | 520.0585
[34 empty] | 34.4 | 0.0001-9.95277030833948i | 0.000000001 | 0.154991081306871+533.169319695634i | 9999999999+9999999i | 0.154991082306871+533.169319695634i | -3781781840.8733+5331694746333.84i | 9999999999.15499+10000532.1693197i | 0.15501950921186+533.169319650679i | 0.15511950921186+523.216549342339i | 34.4 | 523.2166
[34 empty] | 34.6 | 0.0001-9.89523984412942i | 0.000000001 | 0.154991081306871+536.269141321772i | 9999999999+9999999i | 0.154991082306871+536.269141321772i | -3812780054.03486+5362692962592.12i | 9999999999.15499+10000535.2691413i | 0.155019840718278+536.269141276389i | 0.155119840718278+526.37390143226i | 34.6 | 526.3739
Iron-Core Reactor Losses, 60 Hertz |  | SPECIFIED HARMONICS 1: 998.0947; SPECIFIED HARMONICS 3: Watts, 3-Phase or 3406 BTUs/Hour | [24 empty] | 34.8 | 0.0001-9.83837064962293i | 0.000000001 | 0.154991081306871+539.368962947909i | 9999999999+9999999i | 0.154991082306871+539.368962947909i | -3843778267.19641+5393691178850.39i | 9999999999.15499+10000538.3689629i | 0.155020174146473+539.368962902096i | 0.155120174146473+529.530592252473i | 34.8 | 529.5306
Iron-Core Reactor Losses, (harmonic) |  | SPECIFIED HARMONICS 1: 4465.603; SPECIFIED HARMONICS 3: Watts, 3-Phase or 15237 BTUs/Hour | [24 empty] | 35 | 0.0001-9.78215138876794i | 0.000000001 | 0.154991081306871+542.468784574047i | 9999999999+9999999i | 0.154991082306871+542.468784574047i | -3874776480.35797+5424689395108.67i | 9999999999.15499+10000541.4687846i | 0.155020509496449+542.468784527803i | 0.155120509496449+532.686633139035i | 35 | 532.6867
[34 empty] | 35.2 | 0.0001-9.72657098314994i | 0.000000001 | 0.154991081306871+545.568606200184i | 9999999999+9999999i | 0.154991082306871+545.568606200184i | -3905774693.51952+5455687611366.94i | 9999999999.15499+10000544.5686062i | 0.155020846768198+545.568606153506i | 0.155120846768198+535.842035170356i | 35.2 | 535.8421
Total 60 Hz Losses |  | SPECIFIED HARMONICS 1: 1641.0477; SPECIFIED HARMONICS 3: Watts, 3-Phase or 5599 BTUs/Hour | [24 empty] | 35.4 | 0.0001-9.67161860471406i | 0.000000001 | 0.154991081306871+548.668427826322i | 9999999999+9999999i | 0.154991082306871+548.668427826322i | -3936772906.68107+5486685827625.22i | 9999999999.15499+10000547.6684278i | 0.155021185961724+548.668427779209i | 0.155121185961724+538.996809174495i | 35.4 | 538.9968
Total Harmonic Losses |  | SPECIFIED HARMONICS 1: 4465.603; SPECIFIED HARMONICS 3: Watts, 3-Phase or 15237 BTUs/Hour | [24 empty] | 35.6 | 0.0001-9.61728366873252i | 0.000000001 | 0.154991081306871+551.768249452459i | 9999999999+9999999i | 0.154991082306871+551.768249452459i | -3967771119.84262+5517684043883.49i | 9999999999.15499+10000550.7682495i | 0.155021527077032+551.768249404909i | 0.155121527077032+542.150965736177i | 35.6 | 542.151
Total Harmonic Filter Losses |  | SPECIFIED HARMONICS 1: 6106.6508; SPECIFIED HARMONICS 3: Watts, 3-Phase or 20837 BTUs/Hour | [24 empty] | 35.8 | 0.0001-9.56355582700776i | 0.000000001 | 0.154991081306871+554.868071078597i | 9999999999+9999999i | 0.154991082306871+554.868071078597i | -3998769333.00418+5548682260141.77i | 9999999999.15499+10000553.8680711i | 0.155021870114111+554.868071030608i | 0.155121870114111+545.3045152036i | 35.8 | 545.3045
[34 empty] | 36 | 0.0001-9.51042496130216i | 0.000000001 | 0.154991081306871+557.967892704734i | 9999999999+9999999i | 0.154991082306871+557.967892704734i | -4029767546.16573+5579680476400.04i | 9999999999.15499+10000556.9678927i | 0.155022215072967+557.967892656304i | 0.155122215072967+548.457467695002i | 36 | 548.4575
[34 empty] | 36.2 | 0.0001-9.45788117698557i | 0.000000001 | 0.154991081306871+561.067714330872i | 9999999999+9999999i | 0.154991082306871+561.067714330872i | -4060765759.32729+5610678692658.32i | 9999999999.15499+10000560.0677143i | 0.1550225619536+561.067714281999i | 0.1551225619536+551.609833105013i | 36.2 | 551.6099
[34 empty] | 36.4 | 0.0001-9.40591479689224i | 0.000000001 | 0.154991081306871+564.167535957009i | 9999999999+9999999i | 0.154991082306871+564.167535957009i | -4091763972.48884+5641676908916.59i | 9999999999.15499+10000563.167536i | 0.155022910756015+564.167535907691i | 0.155122910756015+554.761621110799i | 36.4 | 554.7616
[34 empty] | 36.6 | 0.0001-9.35451635537917i | 0.000000001 | 0.154991081306871+567.267357583147i | 9999999999+9999999i | 0.154991082306871+567.267357583147i | -4122762185.65039+5672675125174.87i | 9999999999.15499+10000566.2673576i | 0.155023261480203+567.267357533382i | 0.155123261480203+557.912841178003i | 36.6 | 557.9129
[34 empty] | 36.8 | 0.0001-9.3036765925782i | 0.000000001 | 0.154991081306871+570.367179209284i | 9999999999+9999999i | 0.154991082306871+570.367179209284i | -4153760398.81194+5703673341433.14i | 9999999999.15499+10000569.3671792i | 0.155023614126166+570.36717915907i | 0.155123614126166+561.063502566492i | 36.8 | 561.0635
[34 empty] | 37 | 0.0001-9.25338644883453i | 0.000000001 | 0.154991081306871+573.467000835421i | 9999999999+9999999i | 0.154991082306871+573.467000835421i | -4184758611.97349+5734671557691.41i | 9999999999.15499+10000572.4670008i | 0.155023968693907+573.467000784756i | 0.155123968693907+564.213614335922i | 37 | 564.2136
[34 empty] | 37.2 | 0.0001-9.20363705932467i | 0.000000001 | 0.154991081306871+576.566822461559i | 9999999999+9999999i | 0.154991082306871+576.566822461559i | -4215756825.13505+5765669773949.69i | 9999999999.15499+10000575.5668225i | 0.15502432518343+576.566822410442i | 0.15512432518343+567.363185351117i | 37.2 | 567.3632
[34 empty] | 37.4 | 0.0001-9.15441974884699i | 0.000000001 | 0.154991081306871+579.666644087696i | 9999999999+9999999i | 0.154991082306871+579.666644087696i | -4246755038.2966+5796667990207.96i | 9999999999.15499+10000578.6666441i | 0.155024683594724+579.666644036124i | 0.155124683594724+570.512224287277i | 37.4 | 570.5122
[34 empty] | 37.6 | 0.0001-9.10572602677866i | 0.000000001 | 0.154991081306871+582.766465713834i | 9999999999+9999999i | 0.154991082306871+582.766465713834i | -4277753251.45816+5827666206466.24i | 9999999999.15499+10000581.7664657i | 0.155025043927795+582.766465661806i | 0.155125043927795+573.660739635027i | 37.6 | 573.6608
[34 empty] | 37.8 | 0.0001-9.05754758219253i | 0.000000001 | 0.154991081306871+585.866287339971i | 9999999999+9999999i | 0.154991082306871+585.866287339971i | -4308751464.6197+5858664422724.51i | 9999999999.15499+10000584.8662873i | 0.155025406182644+585.866287287484i | 0.155125406182644+576.808739705291i | 37.8 | 576.8088
[34 empty] | 38 | 0.0001-9.00987627912835i | 0.000000001 | 0.154991081306871+588.966108966109i | 9999999999+9999999i | 0.154991082306871+588.966108966109i | -4339749677.78126+5889662638982.79i | 9999999999.15499+10000587.966109i | 0.155025770359275+588.966108913162i | 0.155125770359275+579.956232634034i | 38 | 579.9563
[34 empty] | 38.2 | 0.0001-8.9627041520125i | 0.000000001 | 0.154991081306871+592.065930592246i | 9999999999+9999999i | 0.154991082306871+592.065930592246i | -4370747890.94281+5920660855241.06i | 9999999999.15499+10000591.0659306i | 0.155026136457677+592.065930538837i | 0.155126136457677+583.103226386825i | 38.2 | 583.1032
[34 empty] | 38.4 | 0.0001-8.91602340122077i | 0.000000001 | 0.154991081306871+595.165752218384i | 9999999999+9999999i | 0.154991082306871+595.165752218384i | -4401746104.10437+5951659071499.34i | 9999999999.15499+10000594.1657522i | 0.155026504477855+595.165752164511i | 0.155126504477855+586.24972876329i | 38.4 | 586.2497
[34 empty] | 38.6 | 0.0001-8.86982638877921i | 0.000000001 | 0.154991081306871+598.265573844521i | 9999999999+9999999i | 0.154991082306871+598.265573844521i | -4432744317.26592+5982657287757.61i | 9999999999.15499+10000597.2655738i | 0.155026874419811+598.265573790182i | 0.155126874419811+589.395747401403i | 38.6 | 589.3958
[34 empty] | 38.8 | 0.0001-8.82410563419787i | 0.000000001 | 0.154991081306871+601.365395470659i | 9999999999+9999999i | 0.154991082306871+601.365395470659i | -4463742530.42747+6013655504015.89i | 9999999999.15499+10000600.3653955i | 0.15502724628355+601.365395415851i | 0.15512724628355+592.541289781653i | 38.8 | 592.5413
[34 empty] | 39 | 0.0001-8.77885381043275i | 0.000000001 | 0.154991081306871+604.465217096796i | 9999999999+9999999i | 0.154991082306871+604.465217096796i | -4494740743.58902+6044653720274.16i | 9999999999.15499+10000603.4652171i | 0.15502762006906+604.465217041518i | 0.15512762006906+595.686363231085i | 39 | 595.6864
[34 empty] | 39.2 | 0.0001-8.73406373997136i | 0.000000001 | 0.154991081306871+607.565038722934i | 9999999999+9999999i | 0.154991082306871+607.565038722934i | -4525738956.75058+6075651936532.44i | 9999999999.15499+10000606.5650387i | 0.155027995776346+607.565038667185i | 0.155127995776346+598.830974927214i | 39.2 | 598.831
[34 empty] | 39.4 | 0.0001-8.6897283910375i | 0.000000001 | 0.154991081306871+610.664860349071i | 9999999999+9999999i | 0.154991082306871+610.664860349071i | -4556737169.91213+6106650152790.71i | 9999999999.15499+10000609.6648603i | 0.155028373405409+610.664860292848i | 0.155128373405409+601.97513190181i | 39.4 | 601.9752
[34 empty] | 39.6 | 0.0001-8.64584087391104i | 0.000000001 | 0.154991081306871+613.764681975208i | 9999999999+9999999i | 0.154991082306871+613.764681975208i | -4587735383.07368+6137648369048.98i | 9999999999.15499+10000612.764682i | 0.155028752956255+613.764681918509i | 0.155128752956255+605.118841044598i | 39.6 | 605.1189
[34 empty] | 39.8 | 0.0001-8.60239443735873i | 0.000000001 | 0.154991081306871+616.864503601346i | 9999999999+9999999i | 0.154991082306871+616.864503601346i | -4618733596.23524+6168646585307.26i | 9999999999.15499+10000615.8645036i | 0.155029134428872+616.86450354417i | 0.155129134428872+608.262109106811i | 39.8 | 608.2621
[34 empty] | 40 | 0.0001-8.55938246517193i | 0.000000001 | 0.154991081306871+619.964325227483i | 9999999999+9999999i | 0.154991082306871+619.964325227483i | -4649731809.39678+6199644801565.53i | 9999999999.15499+10000618.9643252i | 0.155029517823267+619.964325169827i | 0.155129517823267+611.404942704655i | 40 | 611.405
[34 empty] | 40.2 | 0.0001-8.51679847280789i | 0.000000001 | 0.154991081306871+623.064146853621i | 9999999999+9999999i | 0.154991082306871+623.064146853621i | -4680730022.55834+6230643017823.81i | 9999999999.15499+10000622.0641469i | 0.155029903139444+623.064146795484i | 0.155129903139444+614.547348322676i | 40.2 | 614.5474
[34 empty] | 40.4 | 0.0001-8.47463610413062i | 0.000000001 | 0.154991081306871+626.163968479758i | 9999999999+9999999i | 0.154991082306871+626.163968479758i | -4711728235.71989+6261641234082.08i | 9999999999.15499+10000625.1639685i | 0.155030290377391+626.163968421137i | 0.155130290377391+617.689332317006i | 40.4 | 617.6894
[34 empty] | 40.6 | 0.0001-8.43288912824821i | 0.000000001 | 0.154991081306871+629.263790105896i | 9999999999+9999999i | 0.154991082306871+629.263790105896i | -4742726448.88145+6292639450340.36i | 9999999999.15499+10000628.2637901i | 0.155030679537116+629.26379004679i | 0.155130679537116+620.830900918542i | 40.6 | 620.8309
[34 empty] | 40.8 | 0.0001-8.39155143644307i | 0.000000001 | 0.154991081306871+632.363611732033i | 9999999999+9999999i | 0.154991082306871+632.363611732033i | -4773724662.043+6323637666598.63i | 9999999999.15499+10000631.3636117i | 0.155031070618617+632.36361167244i | 0.155131070618617+623.972060235997i | 40.8 | 623.9721
[34 empty] | 41 | 0.0001-8.35061703919212i | 0.000000001 | 0.154991081306871+635.463433358171i | 9999999999+9999999i | 0.154991082306871+635.463433358171i | -4804722875.20456+6354635882856.91i | 9999999999.15499+10000634.4634334i | 0.155031463621902+635.463433298088i | 0.155131463621902+627.112816258896i | 41 | 627.1128
[34 empty] | 41.2 | 0.0001-8.31008006327372i | 0.000000001 | 0.154991081306871+638.563254984308i | 9999999999+9999999i | 0.154991082306871+638.563254984308i | -4835721088.36611+6385634099115.18i | 9999999999.15499+10000637.563255i | 0.155031858546957+638.563254923734i | 0.155131858546957+630.25317486046i | 41.2 | 630.2532
[34 empty] | 41.4 | 0.0001-8.26993474895838i | 0.000000001 | 0.154991081306871+641.663076610446i | 9999999999+9999999i | 0.154991082306871+641.663076610446i | -4866719301.52766+6416632315373.46i | 9999999999.15499+10000640.6630766i | 0.15503225539379+641.66307654938i | 0.15513225539379+633.393141800422i | 41.4 | 633.3932
[34 empty] | 41.6 | 0.0001-8.2301754472807i | 0.000000001 | 0.154991081306871+644.762898236583i | 9999999999+9999999i | 0.154991082306871+644.762898236583i | -4897717514.68921+6447630531631.74i | 9999999999.15499+10000643.7628982i | 0.1550326541624+644.762898175023i | 0.1551326541624+636.532722727742i | 41.6 | 636.5327
[34 empty] | 41.8 | 0.0001-8.1907966173894i | 0.000000001 | 0.154991081306871+647.86271986272i | 9999999999+9999999i | 0.154991082306871+647.86271986272i | -4928715727.85076+6478628747890.01i | 9999999999.15499+10000646.8627199i | 0.155033054852792+647.862719800663i | 0.155133054852792+639.671923183274i | 41.8 | 639.6719
[34 empty] | 42 | 0.0001-8.15179282397326i | 0.000000001 | 0.154991081306871+650.962541488858i | 9999999999+9999999i | 0.154991082306871+650.962541488858i | -4959713941.01232+6509626964148.29i | 9999999999.15499+10000649.9625415i | 0.155033457464955+650.962541426302i | 0.155133457464955+642.810748602329i | 42 | 642.8108
[34 empty] | 42.2 | 0.0001-8.11315873476012i | 0.000000001 | 0.154991081306871+654.062363114995i | 9999999999+9999999i | 0.154991082306871+654.062363114995i | -4990712154.17387+6540625180406.56i | 9999999999.15499+10000653.0623631i | 0.155033861998895+654.062363051938i | 0.155133861998895+645.949204317178i | 42.2 | 645.9492
[34 empty] | 42.4 | 0.0001-8.07488911808672i | 0.000000001 | 0.154991081306871+657.162184741133i | 9999999999+9999999i | 0.154991082306871+657.162184741133i | -5021710367.33543+6571623396664.84i | 9999999999.15499+10000656.1621847i | 0.155034268454611+657.162184677574i | 0.155134268454611+649.087295559487i | 42.4 | 649.0873
[34 empty] | 42.6 | 0.0001-8.03697884053702i | 0.000000001 | 0.154991081306871+660.26200636727i | 9999999999+9999999i | 0.154991082306871+660.26200636727i | -5052708580.49697+6602621612923.11i | 9999999999.15499+10000659.2620064i | 0.155034676832112+660.262006303206i | 0.155134676832112+652.225027462669i | 42.6 | 652.225
[34 empty] | 42.8 | 0.0001-7.99942286464666i | 0.000000001 | 0.154991081306871+663.361827993408i | 9999999999+9999999i | 0.154991082306871+663.361827993408i | -5083706793.65853+6633619829181.39i | 9999999999.15499+10000662.361828i | 0.155035087131383+663.361827928838i | 0.155135087131383+655.362405064191i | 42.8 | 655.3624
[34 empty] | 43 | 0.0001-7.96221624667156i | 0.000000001 | 0.154991081306871+666.461649619545i | 9999999999+9999999i | 0.154991082306871+666.461649619545i | -5114705006.82008+6664618045439.66i | 9999999999.15499+10000665.4616496i | 0.15503549935243+666.461649554466i | 0.15513549935243+658.499433307794i | 43 | 658.4995
[34 empty] | 43.2 | 0.0001-7.92535413441845i | 0.000000001 | 0.154991081306871+669.561471245683i | 9999999999+9999999i | 0.154991082306871+669.561471245683i | -5145703219.98164+6695616261697.94i | 9999999999.15499+10000668.5614712i | 0.155035913495254+669.561471180094i | 0.155135913495254+661.636117045676i | 43.2 | 661.6361
[34 empty] | 43.4 | 0.0001-7.88883176513541i | 0.000000001 | 0.154991081306871+672.66129287182i | 9999999999+9999999i | 0.154991082306871+672.66129287182i | -5176701433.14319+6726614477956.21i | 9999999999.15499+10000671.6612929i | 0.155036329559861+672.661292805719i | 0.155136329559861+664.772461040584i | 43.4 | 664.7725
[34 empty] | 43.6 | 0.0001-7.85264446346048i | 0.000000001 | 0.154991081306871+675.761114497958i | 9999999999+9999999i | 0.154991082306871+675.761114497958i | -5207699646.30475+6757612694214.49i | 9999999999.15499+10000674.7611145i | 0.155036747546239+675.761114431343i | 0.155136747546239+667.908469967883i | 43.6 | 667.9085
[34 empty] | 43.8 | 0.0001-7.81678763942641i | 0.000000001 | 0.154991081306871+678.860936124095i | 9999999999+9999999i | 0.154991082306871+678.860936124095i | -5238697859.4663+6788610910472.76i | 9999999999.15499+10000677.8609361i | 0.155037167454394+678.860936056964i | 0.155137167454394+671.044148417538i | 43.8 | 671.0442
[34 empty] | 44 | 0.0001-7.78125678651993i | 0.000000001 | 0.154991081306871+681.960757750233i | 9999999999+9999999i | 0.154991082306871+681.960757750233i | -5269696072.62785+6819609126731.04i | 9999999999.15499+10000680.9607578i | 0.155037589284334+681.960757682584i | 0.155137589284334+674.179500896064i | 44 | 674.1795
[34 empty] | 44.2 | 0.0001-7.74604747979359i | 0.000000001 | 0.154991081306871+685.06057937637i | 9999999999+9999999i | 0.154991082306871+685.06057937637i | -5300694285.7894+6850607342989.31i | 9999999999.15499+10000684.0605794i | 0.155038013036042+685.060579308201i | 0.155138013036042+677.314531828407i | 44.2 | 677.3145
[34 empty] | 44.4 | 0.0001-7.71115537402876i | 0.000000001 | 0.154991081306871+688.160401002507i | 9999999999+9999999i | 0.154991082306871+688.160401002507i | -5331692498.95095+6881605559247.58i | 9999999999.15499+10000687.160401i | 0.155038438709528+688.160400933816i | 0.155138438709528+680.449245559787i | 44.4 | 680.4493
[34 empty] | 44.6 | 0.0001-7.67657620194791i | 0.000000001 | 0.154991081306871+691.260222628645i | 9999999999+9999999i | 0.154991082306871+691.260222628645i | -5362690712.11251+6912603775505.86i | 9999999999.15499+10000690.2602226i | 0.15503886630479+691.26022255943i | 0.15513886630479+683.583646357482i | 44.6 | 683.5837
[34 empty] | 44.8 | 0.0001-7.64230577247493i | 0.000000001 | 0.154991081306871+694.360044254782i | 9999999999+9999999i | 0.154991082306871+694.360044254782i | -5393688925.27406+6943601991764.13i | 9999999999.15499+10000693.3600443i | 0.155039295821836+694.360044185042i | 0.155139295821836+686.717738412567i | 44.8 | 686.7178
[34 empty] | 45 | 0.0001-7.60833996904171i | 0.000000001 | 0.154991081306871+697.45986588092i | 9999999999+9999999i | 0.154991082306871+697.45986588092i | -5424687138.43561+6974600208022.41i | 9999999999.15499+10000696.4598659i | 0.155039727260653+697.459865810652i | 0.155139727260653+689.85152584161i | 45 | 689.8515
[34 empty] | 45.2 | 0.0001-7.57467474793975i | 0.000000001 | 0.154991081306871+700.559687507057i | 9999999999+9999999i | 0.154991082306871+700.559687507057i | -5455685351.59716+7005598424280.68i | 9999999999.15499+10000699.5596875i | 0.155040160621246+700.559687436259i | 0.155140160621246+692.985012688319i | 45.2 | 692.985
[34 empty] | 45.4 | 0.0001-7.54130613671535i | 0.000000001 | 0.154991081306871+703.659509133195i | 9999999999+9999999i | 0.154991082306871+703.659509133195i | -5486683564.75872+7036596640538.96i | 9999999999.15499+10000702.6595091i | 0.155040595903616+703.659509061866i | 0.155140595903616+696.118202925151i | 45.4 | 696.1182
[34 empty] | 45.6 | 0.0001-7.50823023260694i | 0.000000001 | 0.154991081306871+706.759330759332i | 9999999999+9999999i | 0.154991082306871+706.759330759332i | -5517681777.92027+7067594856797.23i | 9999999999.15499+10000705.7593308i | 0.15504103310777+706.75933068747i | 0.15514103310777+699.251100454863i | 45.6 | 699.2511
[34 empty] | 45.8 | 0.0001-7.47544320102351i | 0.000000001 | 0.154991081306871+709.85915238547i | 9999999999+9999999i | 0.154991082306871+709.85915238547i | -5548679991.08183+7098593073055.51i | 9999999999.15499+10000708.8591524i | 0.155041472233694+709.859152313072i | 0.155141472233694+702.383709112048i | 45.8 | 702.3837
[34 empty] | 46 | 0.0001-7.44294127406254i | 0.000000001 | 0.154991081306871+712.958974011607i | 9999999999+9999999i | 0.154991082306871+712.958974011607i | -5579678204.24338+7129591289313.78i | 9999999999.15499+10000711.958974i | 0.155041913281394+712.958973938672i | 0.155141913281394+705.516032664609i | 46 | 705.516
[34 empty] | 46.2 | 0.0001-7.41072074906659i | 0.000000001 | 0.154991081306871+716.058795637745i | 9999999999+9999999i | 0.154991082306871+716.058795637745i | -5610676417.40493+7160589505572.06i | 9999999999.15499+10000715.0587956i | 0.155042356250873+716.058795564271i | 0.155142356250873+708.648074815204i | 46.2 | 708.6481
[34 empty] | 46.4 | 0.0001-7.37877798721717i | 0.000000001 | 0.154991081306871+719.158617263882i | 9999999999+9999999i | 0.154991082306871+719.158617263882i | -5641674630.56648+7191587721830.33i | 9999999999.15499+10000718.1586173i | 0.155042801142134+719.158617189867i | 0.155142801142134+711.77983920265i | 46.4 | 711.7799
[34 empty] | 46.6 | 0.0001-7.34710941216473i | 0.000000001 | 0.154991081306871+722.25843889002i | 9999999999+9999999i | 0.154991082306871+722.25843889002i | -5672672843.72804+7222585938088.61i | 9999999999.15499+10000721.2584389i | 0.155043247955166+722.258438815462i | 0.155143247955166+714.911329403297i | 46.6 | 714.9113
[34 empty] | 46.8 | 0.0001-7.31571150869394i | 0.000000001 | 0.154991081306871+725.358260516157i | 9999999999+9999999i | 0.154991082306871+725.358260516157i | -5703671056.88959+7253584154346.88i | 9999999999.15499+10000724.3582605i | 0.155043696689974+725.358260441054i | 0.155143696689974+718.04254893236i | 46.8 | 718.0426
[34 empty] | 47 | 0.0001-7.28458082142291i | 0.000000001 | 0.154991081306871+728.458082142294i | 9999999999+9999999i | 0.154991082306871+728.458082142294i | -5734669270.05114+7284582370605.15i | 9999999999.15499+10000727.4580821i | 0.155044147346559+728.458082066644i | 0.155144147346559+721.173501245221i | 47 | 721.1735
[34 empty] | 47.2 | 0.0001-7.25371395353552i | 0.000000001 | 0.154991081306871+731.557903768432i | 9999999999+9999999i | 0.154991082306871+731.557903768432i | -5765667483.2127+7315580586863.43i | 9999999999.15499+10000730.5579038i | 0.155044599924928+731.557903692234i | 0.155144599924928+724.304189738698i | 47.2 | 724.3042
[34 empty] | 47.4 | 0.0001-7.22310756554592i | 0.000000001 | 0.154991081306871+734.657725394569i | 9999999999+9999999i | 0.154991082306871+734.657725394569i | -5796665696.37424+7346578803121.7i | 9999999999.15499+10000733.6577254i | 0.155045054425068+734.65772531782i | 0.155145054425068+727.434617752274i | 47.4 | 727.4346
[34 empty] | 47.6 | 0.0001-7.19275837409404i | 0.000000001 | 0.154991081306871+737.757547020707i | 9999999999+9999999i | 0.154991082306871+737.757547020707i | -5827663909.5358+7377577019379.98i | 9999999999.15499+10000736.757547i | 0.155045510846984+737.757546943405i | 0.155145510846984+730.564788569311i | 47.6 | 730.5648
[34 empty] | 47.8 | 0.0001-7.16266315077147i | 0.000000001 | 0.154991081306871+740.857368646844i | 9999999999+9999999i | 0.154991082306871+740.857368646844i | -5858662122.69735+7408575235638.25i | 9999999999.15499+10000739.8573686i | 0.155045969190676+740.857368568988i | 0.155145969190676+733.694705418217i | 47.8 | 733.6947
[34 empty] | 48 | 0.0001-7.13281872097659i | 0.000000001 | 0.154991081306871+743.957190272982i | 9999999999+9999999i | 0.154991082306871+743.957190272982i | -5889660335.85891+7439573451896.53i | 9999999999.15499+10000742.9571903i | 0.155046429456153+743.95719019457i | 0.155146429456153+736.824371473593i | 48 | 736.8244
[34 empty] | 48.2 | 0.0001-7.10322196279827i | 0.000000001 | 0.154991081306871+747.057011899119i | 9999999999+9999999i | 0.154991082306871+747.057011899119i | -5920658549.02046+7470571668154.8i | 9999999999.15499+10000746.0570119i | 0.1550468916434+747.057011820148i | 0.1551468916434+739.95378985735i | 48.2 | 739.9538
[34 empty] | 48.4 | 0.0001-7.0738698059272i | 0.000000001 | 0.154991081306871+750.156833525257i | 9999999999+9999999i | 0.154991082306871+750.156833525257i | -5951656762.18202+7501569884413.08i | 9999999999.15499+10000749.1568335i | 0.155047355752423+750.156833445726i | 0.155147355752423+743.082963639799i | 48.4 | 743.083
[34 empty] | 48.6 | 0.0001-7.04475923059417i | 0.000000001 | 0.154991081306871+753.256655151394i | 9999999999+9999999i | 0.154991082306871+753.256655151394i | -5982654975.34357+7532568100671.35i | 9999999999.15499+10000752.2566552i | 0.15504782178323+753.256655071301i | 0.15514782178323+746.211895840707i | 48.6 | 746.2119
[34 empty] | 48.8 | 0.0001-7.01588726653435i | 0.000000001 | 0.154991081306871+756.356476777531i | 9999999999+9999999i | 0.154991082306871+756.356476777531i | -6013653188.50511+7563566316929.62i | 9999999999.15499+10000755.3564768i | 0.155048289735809+756.356476696874i | 0.155148289735809+749.34058943034i | 48.8 | 749.3406
[34 empty] | 49 | 0.0001-6.98725099197707i | 0.000000001 | 0.154991081306871+759.456298403669i | 9999999999+9999999i | 0.154991082306871+759.456298403669i | -6044651401.66667+7594564533187.9i | 9999999999.15499+10000758.4562984i | 0.155048759610163+759.456298322445i | 0.155148759610163+752.469047330468i | 49 | 752.4691
[34 empty] | 49.2 | 0.0001-6.95884753266009i | 0.000000001 | 0.154991081306871+762.556120029806i | 9999999999+9999999i | 0.154991082306871+762.556120029806i | -6075649614.82822+7625562749446.17i | 9999999999.15499+10000761.55612i | 0.155049231406293+762.556119948015i | 0.155149231406293+755.597272415355i | 49.2 | 755.5973
[34 empty] | 49.4 | 0.0001-6.93067406086794i | 0.000000001 | 0.154991081306871+765.655941655944i | 9999999999+9999999i | 0.154991082306871+765.655941655944i | -6106647827.98978+7656560965704.45i | 9999999999.15499+10000764.6559417i | 0.155049705124209+765.655941573583i | 0.155149705124209+758.725267512715i | 49.4 | 758.7253
[34 empty] | 49.6 | 0.0001-6.90272779449348i | 0.000000001 | 0.154991081306871+768.755763282081i | 9999999999+9999999i | 0.154991082306871+768.755763282081i | -6137646041.15133+7687559181962.72i | 9999999999.15499+10000767.7557633i | 0.155050180763893+768.755763199148i | 0.155150180763893+761.853035404655i | 49.6 | 761.8531
[34 empty] | 49.8 | 0.0001-6.87500599612201i | 0.000000001 | 0.154991081306871+771.855584908219i | 9999999999+9999999i | 0.154991082306871+771.855584908219i | -6168644254.31289+7718557398221i | 9999999999.15499+10000770.8555849i | 0.155050658325355+771.855584824712i | 0.155150658325355+764.98057882859i | 49.8 | 764.9806
[34 empty] | 50 | 0.0001-6.84750597213753i | 0.000000001 | 0.154991081306871+774.955406534356i | 9999999999+9999999i | 0.154991082306871+774.955406534356i | -6199642467.47443+7749555614479.27i | 9999999999.15499+10000773.9554065i | 0.155051137808594+774.955406450273i | 0.155151137808594+768.107900478135i | 50 | 768.1079
(mH)
𝐻=𝑋_𝐿/2𝜋𝑓×1000 (mH)
(kvar/phase)
〖𝑄_(𝑅𝐴𝑇𝐸𝐷 𝑃𝐸𝑅 𝑃𝐻𝐴𝑆𝐸) =(𝑉_(𝐶𝐴𝑃 𝑅𝐴𝑇𝐼𝑁𝐺) )^2/𝑋_𝐶 ×1000〗_(kvar/phase)
(kV)
V_(CAP FUNDAMENTAL VOLTAGE)=I_(RATED FUNDAMENTAL)× X_C/1000 (kV)
𝑉_(𝐶𝐴𝑃 𝐻𝐴𝑅𝑀𝑂𝑁𝐼𝐶 𝑉𝑂𝐿𝑇𝐴𝐺𝐸)=𝑋_𝐶/𝑛×𝐼_𝑛
(amps/capacitor)
𝐼_𝐶𝐴𝑃= 𝐼_(𝑅𝐴𝑇𝐸𝐷 𝐹𝑈𝑁𝐷𝐴𝑀𝐸𝑁𝑇𝐴𝐿)/𝑁 (amps/capacitor)
𝐼_(𝑅𝐸𝑆𝐼𝑆𝑇𝑂𝑅 (𝑛))=𝑋_𝐿/〖𝑅+𝑗𝑋〗_𝐿 ×𝐼_𝑛
𝐼_(𝑅𝐸𝐴𝐶𝑇𝑂𝑅 (𝑛))=𝑅/〖𝑅+𝑗𝑋〗_𝐿 ×𝐼_𝑛
(ohms)
𝑋_𝑒𝑓𝑓= 〖〖𝑘𝑉〗_𝐿𝐿𝑆𝑌𝑆〗^2/(𝑄_𝑒𝑓𝑓 (𝑀𝑉𝐴𝑅)) (ohms)
𝐼_(𝐹𝐼𝐿𝑇𝐸𝑅 𝑅𝑀𝑆 𝐶𝑈𝑅𝑅𝐸𝑁𝑇)=√(∑_(𝑛=1)^𝑛▒〖〖𝐼_𝑛^ 〗_^2 (𝑎𝑚𝑝𝑠)〗)
(amps)
𝐼_(𝑅𝐴𝑇𝐸𝐷 𝐹𝑈𝑁𝐷𝐴𝑀𝐸𝑁𝑇𝐴𝐿)= 𝑄_𝑒𝑓𝑓/(1.73×〖〖𝑘𝑉〗_𝐿𝐿𝑆𝑌𝑆〗^ ) (amps)
(ohms)
𝑋_𝐶=(ℎ^2/(ℎ^2−1)) 𝑋_𝑒𝑓𝑓 (ohms)
(ohms)
𝑋_𝐿=𝑋_𝐶/ℎ^2 (ohms)
(amps)
𝐼_𝐹𝑈𝑆𝐸≥ 𝐼_𝐶𝐴𝑃×1.8 (amps)
/1000 (kV)
𝑉_(𝐶𝐴𝑃 𝑅𝑀𝑆 𝑉𝑂𝐿𝑇𝐴𝐺𝐸)=√(∑_(𝑛=1)^𝑛▒〖𝑉_(𝐶𝐴𝑃 𝐻𝐴𝑅𝑀𝑂𝑁𝐼𝐶 𝑉𝑂𝐿𝑇𝐴𝐺𝐸 (𝑉𝑂𝐿𝑇𝑆))〗^2 ) /1000 (kV)
𝑉_(𝐶𝐴𝑃 𝑃𝐸𝐴𝐾 𝑉𝑂𝐿𝑇𝐴𝐺𝐸)=1.414 ×∑_(𝑛=1)^𝑛▒〖𝑉_(𝐶𝐴𝑃 𝐻𝐴𝑅𝑀𝑂𝑁𝐼𝐶 𝑉𝑂𝐿𝑇𝐴𝐺𝐸)〗^
/N
𝐼_(𝐶𝐴𝑃 𝑅𝑀𝑆 𝐶𝑈𝑅𝑅𝐸𝑁𝑇)=√(∑_(𝑛=1)^𝑛▒〖𝐼_𝑛^ 〗_^2 ) /N
/1000
𝑄_( 𝐶𝐴𝑃𝐴𝐶𝐼𝑇𝑂𝑅)=∑_(𝑛=1)^𝑛▒〖〖𝑋_𝑐/𝑛 𝑥 𝐼〗_𝑛^ 〗_^2 /1000

## High-Pass Filter Design
Rev: 7-27-2020 | [10 empty] | Click here to learn how to use this spreadsheet tool. You will be redirected to our YouTube Channel: https://youtu.be/sV6w9_-4ZJw | [23 empty] | PLOT (ohms) |  |  | (res branch) | (aux branch) | product of res branch and aux branch | sum of res branch and aux branch | power over sum rule of aux and res branch | add main cap in |  |  | SD - Standard Duty Capacitors, with -40C to +55C Temperature Rating
[34 empty] | HARM # | Xc main | Xc aux | XL (inductance) | Resistance | XCAUX + XL | [6 empty] | HD- Heavy Duty Capacitors, with -40C to +55C Temperature Rating
Northeast Power Systems, Inc. | [10 empty] | Contact NEPSI for assistance or to obtain a quote on your metal-enclosed harmonic filter system. Email us at: sales@nepsi.com | [22 empty] | 1 | 0.0001-11.0913488372093i | 0.000000001 | 0.000192558139534884+0.0192558139534884i | 2.30607627906977+0.0001i | 0.000192559139534884+0.0192558139534884i | 0.000442130482604133+0.0444053950482342i | 2.3062688382093+0.0193558139534884i | 0.000353278019832645+0.0192512496067378i | 0.000453278019832645-11.0720975876026i | 1 | 11.0721 | EXD - Extreme Duty Capacitors, with -50C to +55C Temperature Rating
66 Carey Road, Queensbury, NY |  |  |  |  | Phone: (518) 792-4776 Fax: (518) 792-5767 www.nepsi.com | [28 empty] | 1.2 | 0.0001-9.24279069767442i | 0.000000001 | 0.000192558139534884+0.0231069767441861i | 2.30607627906977+0.0001i | 0.000192559139534884+0.0231069767441861i | 0.000441745366325063+0.0532864702066983i | 2.3062688382093+0.0232069767441861i | 0.000423994302393779+0.0231007893347549i | 0.000523994302393779-9.21968990833967i | 1.2 | 9.2197
[34 empty] | 1.4 | 0.0001-7.92239202657808i | 0.000000001 | 0.000192558139534884+0.0269581395348837i | 2.30607627906977+0.0001i | 0.000192559139534884+0.0269581395348837i | 0.000441360250045994+0.0621675453651622i | 2.3062688382093+0.0270581395348837i | 0.000507562485600121+0.0269499421051292i | 0.000607562485600121-7.89544208447295i | 1.4 | 7.8954
FILTER BANK DESIGN CALCULATIONS - HIGH-PASS FILTER DESIGN | [10 empty] | REVERSE CALCULATION USING C AND L | [22 empty] | 1.6 | 0.0001-6.93209302325582i | 0.000000001 | 0.000192558139534884+0.0308093023255814i | 2.30607627906977+0.0001i | 0.000192559139534884+0.0308093023255814i | 0.000440975133766924+0.0710486205236263i | 2.3062688382093+0.0309093023255814i | 0.000603979768572232+0.0307986435724953i | 0.000703979768572232-6.90129437968332i | 1.6 | 6.9013
[34 empty] | 1.8 | 0.0001-6.16186046511628i | 0.000000001 | 0.000192558139534884+0.0346604651162791i | 2.30607627906977+0.0001i | 0.000192559139534884+0.0346604651162791i | 0.000440590017487854+0.0799296956820904i | 2.3062688382093+0.0347604651162791i | 0.000713242921017318+0.0346468294166681i | 0.000813242921017318-6.12721363569961i | 1.8 | 6.1272
kVLLsys (System Line-to-Line Voltage Rating) |  | 6.9 | kV |  |  | Job Name: | Enter Job Name |  |  |  | CAPACITANCE (µf) | 13.3 | (µf) | [20 empty] | 2 | 0.0001-5.54567441860465i | 0.000000001 | 0.000192558139534884+0.0385116279069767i | 2.30607627906977+0.0001i | 0.000192559139534884+0.0385116279069767i | 0.000440204901208784+0.0888107708405543i | 2.3062688382093+0.0386116279069767i | 0.000835348283499428+0.038494435346224i | 0.000935348283499428-5.50717998325843i | 2 | 5.5072 |  | DF (Damping Factor) | 499
Qeff (3-Phase Output Rating of Filter) |  | 4300 | kvar |  |  | Stage/Branch Name | Branch/Stage # |  |  |  | INDUCTANCE (mH) | 23.95 | mH | [20 empty] | 2.2 | 0.0001-5.0415221987315i | 0.000000001 | 0.000192558139534884+0.0423627906976744i | 2.30607627906977+0.0001i | 0.000192559139534884+0.0423627906976744i | 0.000439819784929715+0.0976918459990184i | 2.3062688382093+0.0424627906976744i | 0.000970291767745467+0.0423413971020784i | 0.00107029176774547-4.99918080162942i | 2.2 | 4.9992
h (Tuning Point of Filter) |  | 24 | (harmonic #) | [7 empty] | XL (Ohms) | 9.0287 | Ohms |  |  |  |  | EasyPower Input - Filter Input Data | [15 empty] | 2.4 | 0.0001-4.62139534883721i | 0.000000001 | 0.000192558139534884+0.0462139534883721i | 2.30607627906977+0.0001i | 0.000192559139534884+0.0462139534883721i | 0.000439434668650645+0.106572921157483i | 2.3062688382093+0.0463139534883721i | 0.00111806885698696+0.046187650461059i | 0.00121806885698696-4.57520769837615i | 2.4 | 4.5752
f (System Frequency) |  | 60 | (HZ) | [7 empty] | Xc (Ohms) | 199.4482 | Ohms | [20 empty] | 2.6 | 0.0001-4.26590339892666i | 0.000000001 | 0.000192558139534884+0.0500651162790698i | 2.30607627906977+0.0001i | 0.000192559139534884+0.0500651162790698i | 0.000439049552371575+0.115453996315947i | 2.3062688382093+0.0501651162790698i | 0.00127867460633753+0.0500331312394748i | 0.00137867460633753-4.21587026768719i | 2.6 | 4.2159
hFrequency |  | 1440 | Hz | [7 empty] | h (Tuning Point) | 4.7001 | [6 empty] | Resistor | 2.3061 |  | Ohms | [11 empty] | 2.8 | 0.0001-3.96119601328904i | 0.000000001 | 0.000192558139534884+0.0539162790697675i | 2.30607627906977+0.0001i | 0.000192559139534884+0.0539162790697675i | 0.000438664436092505+0.124335071474411i | 2.3062688382093+0.0540162790697675i | 0.00145210364320606+0.0538777752966824i | 0.00155210364320606-3.90731823799236i | 2.8 | 3.9073
Xeff (effective reactance of Filter Bank) |  | 11.0721 | Ohms | [15 empty] | Inductor | 0.00019256 |  | + j | 0.019256 |  | Ohms | [8 empty] | 3 | 0.0001-3.69711627906977i | 0.000000001 | 0.000192558139534884+0.0577674418604651i | 2.30607627906977+0.0001i | 0.000192559139534884+0.0577674418604651i | 0.000438279319813435+0.133216146632875i | 2.3062688382093+0.0578674418604651i | 0.0016383501677454+0.0577215185386444i | 0.0017383501677454-3.63939476053113i | 3 | 3.6394
IRATED FUNDAMENTAL |  | 360.2245 | amps | [7 empty] | Qeff | 0.25003 | MVAR | [5 empty] | Capacitor Bank 1: | 2.0773 |  | MVAR @ | 8.304 |  | kV (LL) | [8 empty] | 3.2 | 0.0001-3.46604651162791i | 0.000000001 | 0.000192558139534884+0.0616186046511628i | 2.30607627906977+0.0001i | 0.000192559139534884+0.0616186046511628i | 0.000437894203534366+0.142097221791339i | 2.3062688382093+0.0617186046511628i | 0.00183740795333666+0.0615642969214844i | 0.00193740795333666-3.40448221470643i | 3.2 | 3.4045
IFILTER RMS CURRENT |  | 373.8472 | amps | [15 empty] | Capacitor Bank 1: | N/A |  | MVAR @ | N/A |  | kV (LL) | [8 empty] | 3.4 | 0.0001-3.26216142270862i | 0.000000001 | 0.000192558139534884+0.0654697674418605i | 2.30607627906977+0.0001i | 0.000192559139534884+0.0654697674418605i | 0.000437509087255296+0.150978296949803i | 2.3062688382093+0.0655697674418605i | 0.00204927034710884+0.0654060464550352i | 0.00214927034710884-3.19675537625358i | 3.4 | 3.1968
DF (Damping Factor) |  | 4.99 | [8 empty] | CAPACITANCE CALCULATOR | [22 empty] | 3.6 | 0.0001-3.08093023255814i | 0.000000001 | 0.000192558139534884+0.0693209302325582i | 2.30607627906977+0.0001i | 0.000192559139534884+0.0693209302325582i | 0.000437123970976226+0.159859372108267i | 2.3062688382093+0.0694209302325582i | 0.00227393027049397+0.0692467032063814i | 0.00237393027049397-3.01168352935176i | 3.6 | 3.0117
R (Resistor Ohm Rating/Phase) |  | 2.3061 | Ohms | [30 empty] | 3.8 | 0.0001-2.91877600979192i | 0.000000001 | 0.000192558139534884+0.0731720930232558i | 2.30607627906977+0.0001i | 0.000192559139534884+0.0731720930232558i | 0.000436738854697156+0.168740447266731i | 2.3062688382093+0.0732720930232558i | 0.00251138021981738+0.0730862033033943i | 0.00261138021981738-2.84568980648853i | 3.8 | 2.8457
(Rw) (Resistor KW/Phase) |  | 0.060989 | kW/Phase | [7 empty] | CAPACITOR KVAR | 1320 | kvar | [20 empty] | 4 | 0.0001-2.77283720930233i | 0.000000001 | 0.000192558139534884+0.0770232558139535i | 2.30607627906977+0.0001i | 0.000192559139534884+0.0770232558139535i | 0.000436353738418087+0.177621522425195i | 2.3062688382093+0.0771232558139535i | 0.00276161226692327+0.0769244829382609i | 0.00286161226692327-2.69591272636407i | 4 | 2.6959
Ifundamental resistor current (actual) |  | 5.1427 | amps | [7 empty] | CAPACITOR FREQUENCY | 50 | Hertz | [20 empty] | 4.2 | 0.0001-2.64079734219269i | 0.000000001 | 0.000192558139534884+0.0808744186046512i | 2.30607627906977+0.0001i | 0.000192559139534884+0.0808744186046512i | 0.000435968622139017+0.186502597583659i | 2.3062688382093+0.0809744186046512i | 0.00302461805983531+0.0807614783710048i | 0.00312461805983531-2.56003586382168i | 4.2 | 2.56
(Rw) (Resistor KW/Phase - Specified) |  | 0.091484 | kW/Phase | (at least 1.5X is recommended, if not 2X actual) | [6 empty] | CAPACITOR VOLTAGE (kV) | 16 | kV | [20 empty] | 4.4 | 0.0001-2.52076109936575i | 0.000000001 | 0.000192558139534884+0.0847255813953489i | 2.30607627906977+0.0001i | 0.000192559139534884+0.0847255813953489i | 0.000435583505859947+0.195383672742123i | 2.3062688382093+0.0848255813953489i | 0.00330038882345222+0.0845971259329988i | 0.00340038882345222-2.43616397343275i | 4.4 | 2.4362
Ifundamental resistor current (specified) |  | 6.2985 | amps | [7 empty] | CAPACITANCE (µf) | 16.41 | (µf) | [20 empty] | 4.6 | 0.0001-2.41116279069767i | 0.000000001 | 0.000192558139534884+0.0885767441860466i | 2.30607627906977+0.0001i | 0.000192559139534884+0.0885767441860466i | 0.000435198389580877+0.204264747900587i | 2.3062688382093+0.0886767441860466i | 0.0035889153602783+0.0884313620304701i | 0.0036889153602783-2.3227314286672i | 4.6 | 2.3227
Xc |  | 11.0913 | Ohms | [5 empty] | Capacitance (per phase): | 239.16 micro-farads/Phase | Xc (Ohms) | 193.9394 | Ohms | [20 empty] | 4.8 | 0.0001-2.3106976744186i | 0.000000001 | 0.000192558139534884+0.0924279069767442i | 2.30607627906977+0.0001i | 0.000192559139534884+0.0924279069767442i | 0.000434813273301808+0.213145823059051i | 2.3062688382093+0.0925279069767442i | 0.00389018805118861+0.092264123147996i | 0.00399018805118861-2.2184335512706i | 4.8 | 2.2184
[11 empty] | RATED CURRENT | 82.5 | AMPS | [20 empty] | 5 | 0.0001-2.21826976744186i | 0.000000001 | 0.000192558139534884+0.0962790697674419i | 2.30607627906977+0.0001i | 0.000192559139534884+0.0962790697674419i | 0.000434428157022738+0.222026898217515i | 2.3062688382093+0.0963790697674419i | 0.00420419685622891+0.0960953458519911i | 0.00430419685622891-2.12217442158987i | 5 | 2.1222
XL (Inductive reactance of reactor at system frequency) |  | 0.019256 | ohms | [30 empty] | 5.2 | 0.0001-2.13295169946333i | 0.000000001 | 0.000192558139534884+0.10013023255814i | 2.30607627906977+0.0001i | 0.000192559139534884+0.10013023255814i | 0.000434043040743668+0.23090797337598i | 2.3062688382093+0.10023023255814i | 0.0045309313154501+0.0999249667941848i | 0.0046309313154501-2.03302673266915i | 5.2 | 2.033
H (Inductance of Reactor) |  | 0.051079 | mH | [24 empty] | ETAP 19.5.0 - INPUT EDITOR | [5 empty] | 5.4 | 0.0001-2.05395348837209i | 0.000000001 | 0.000192558139534884+0.103981395348837i | 2.30607627906977+0.0001i | 0.000192559139534884+0.103981395348837i | 0.000433657924464598+0.239789048534443i | 2.3062688382093+0.104081395348837i | 0.00487038054977678+0.103752922715087i | 0.00497038054977678-1.950200565657i | 5.4 | 1.9502
XX/R RATIO (X/R OF IRON-CORE REACTOR AT FUNDAMENTAL FREQUENCY) |  | 100 | Typically Near 100 | [30 empty] | 5.6 | 0.0001-1.98059800664452i | 0.000000001 | 0.000192558139534884+0.107832558139535i | 2.30607627906977+0.0001i | 0.000192559139534884+0.107832558139535i | 0.000433272808185528+0.248670123692907i | 2.3062688382093+0.107932558139535i | 0.00522253326191084+0.107579150447448i | 0.00532253326191084-1.87301885619707i | 5.6 | 1.873
[34 empty] | 5.8 | 0.0001-1.91230152365678i | 0.000000001 | 0.000192558139534884+0.111683720930233i | 2.30607627906977+0.0001i | 0.000192559139534884+0.111683720930233i | 0.000432887691906459+0.257551198851372i | 2.3062688382093+0.111783720930233i | 0.00558737773726807+0.111403586919705i | 0.00568737773726807-1.80089793673707i | 5.8 | 1.8009
CAPACITOR PARAMETERS | [33 empty] | 6 | 0.0001-1.84855813953488i | 0.000000001 | 0.000192558139534884+0.11553488372093i | 2.30607627906977+0.0001i | 0.000192559139534884+0.11553488372093i | 0.000432502575627389+0.266432274009835i | 2.3062688382093+0.11563488372093i | 0.00596490184494955+0.115226169159413i | 0.00606490184494955-1.73333197037547i | 6 | 1.7333
VCAP RATING |  | 4.8 | kV | [14 empty] | ETAP Input Data | [15 empty] | 6.2 | 0.0001-1.78892723180795i | 0.000000001 | 0.000192558139534884+0.119386046511628i | 2.30607627906977+0.0001i | 0.000192559139534884+0.119386046511628i | 0.000432117459348319+0.2753133491683i | 2.3062688382093+0.119486046511628i | 0.00635509303874691+0.119046834296675i | 0.00645509303874691-1.66988039751128i | 6.2 | 1.6699
QRATED PER PHASE |  | 2077.2947 | kvar | [16 empty] | Capacitor C1 |  |  | Inductor L1 | [10 empty] | 6.4 | 0.0001-1.73302325581395i | 0.000000001 | 0.000192558139534884+0.123237209302326i | 2.30607627906977+0.0001i | 0.000192559139534884+0.123237209302326i | 0.000431732343069249+0.284194424326764i | 2.3062688382093+0.123337209302326i | 0.00675793835818043+0.122865519567547i | 0.00685793835818043-1.6101577362464i | 6.4 | 1.6102
Number of Caps Per Phase (N) |  | 2 | [5 empty] | Main Cap Capacitive Reactance (per can): | 22.1827 | Ohms/Capacitor | [8 empty] | KVAR | 2077.2947 |  | XL1 | 0.019256 |  | ohms | [8 empty] | 6.6 | 0.0001-1.68050739957717i | 0.000000001 | 0.000192558139534884+0.127088372093023i | 2.30607627906977+0.0001i | 0.000192559139534884+0.127088372093023i | 0.00043134722679018+0.293075499485227i | 2.3062688382093+0.127188372093023i | 0.00717342442957155+0.126682162317446i | 0.00727342442957155-1.55382523725972i | 6.6 | 1.5538
Capacitor Can KVAR Rating (kvar) |  | 1038.6473 | kvar |  |  |  |  | Main Cap Capacitance (per can): | 119.5824 | µF (micro-farads)/Capacitor | [8 empty] | Uf | 239.16 |  | Q Factor | 100 | [10 empty] | 6.8 | 0.0001-1.63108071135431i | 0.000000001 | 0.000192558139534884+0.130939534883721i | 2.30607627906977+0.0001i | 0.000192559139534884+0.130939534883721i | 0.00043096211051111+0.301956574643692i | 2.3062688382093+0.131039534883721i | 0.00760153746714859+0.13049670000453i | 0.00770153746714859-1.50058401134978i | 6.8 | 1.5006
ICAP (Fundamental Amps Each Capacitor) |  | 180.1123 | amps | [15 empty] | Rated kV | 4.8 |  | Max I | 373.8118 |  | Amps | [8 empty] | 7 | 0.0001-1.58447840531561i | 0.000000001 | 0.000192558139534884+0.134790697674419i | 2.30607627906977+0.0001i | 0.000192559139534884+0.134790697674419i | 0.00043057699423204+0.310837649802156i | 2.3062688382093+0.134890697674419i | 0.0080422632741848+0.134309070203076i | 0.0081422632741848-1.45016933511253i | 7 | 1.4502
IFUSE (Minimum Recommended Fuse Rating on each Capacitors) |  | 324.2021 | amps | [15 empty] | Max. KV | 5.28 | [13 empty] | 7.2 | 0.0001-1.54046511627907i | 0.000000001 | 0.000192558139534884+0.138641860465116i | 2.30607627906977+0.0001i | 0.000192559139534884+0.138641860465116i | 0.00043019187795297+0.319718724960619i | 2.3062688382093+0.138741860465116i | 0.00849558724417054+0.138119210606838i | 0.00859558724417054-1.40234590567223i | 7.2 | 1.4024
VCAP FUNDAMENTAL VOLTAGE |  | 3.9954 | kV | [19 empty] | Resistor | [10 empty] | 7.4 | 0.0001-1.4988309239472i | 0.000000001 | 0.000192558139534884+0.142493023255814i | 2.30607627906977+0.0001i | 0.000192559139534884+0.142493023255814i | 0.000429806761673901+0.328599800119084i | 2.3062688382093+0.142593023255814i | 0.00896149436201784+0.141927059032399i | 0.00906149436201784-1.3569038649148i | 7.4 | 1.3569
VCAP RMS VOLTAGE |  | 4.0015 | kV | [18 empty] | R1 | 2.3061 | [10 empty] | 7.6 | 0.0001-1.45938800489596i | 0.000000001 | 0.000192558139534884+0.146344186046512i | 2.30607627906977+0.0001i | 0.000192559139534884+0.146344186046512i | 0.000429421645394831+0.337480875277549i | 2.3062688382093+0.146444186046512i | 0.0094399692052971+0.145732553422496i | 0.0095399692052971-1.31365545147346i | 7.6 | 1.3137
VPEAK CAP VOLTAGE |  | 5.9631 | kV | [30 empty] | 7.8 | 0.0001-1.42196779964222i | 0.000000001 | 0.000192558139534884+0.150195348837209i | 2.30607627906977+0.0001i | 0.000192559139534884+0.150195348837209i | 0.000429036529115761+0.346361950436011i | 2.3062688382093+0.150295348837209i | 0.00993099594550686+0.149535631849344i | 0.0100309959455069-1.27243216779288i | 7.8 | 1.2725
ICAP RMS CURRENT |  | 186.9236 | amps | [30 empty] | 8 | 0.0001-1.38641860465116i | 0.000000001 | 0.000192558139534884+0.154046511627907i | 2.30607627906977+0.0001i | 0.000192559139534884+0.154046511627907i | 0.000428651412836691+0.355243025594476i | 2.3062688382093+0.154146511627907i | 0.0104345583493761+0.153336232517941i | 0.0105345583493761-1.23308237213322i | 8 | 1.2331
QCAPACITROR (1-phase) |  | 1461.415 | kvar | [30 empty] | 8.2 | 0.0001-1.35260351673284i | 0.000000001 | 0.000192558139534884+0.157897674418605i | 2.30607627906977+0.0001i | 0.000192559139534884+0.157897674418605i | 0.000428266296557621+0.364124100752941i | 2.3062688382093+0.157997674418605i | 0.0109506397801975+0.157134293769348i | 0.0110506397801975-1.19546922296349i | 8.2 | 1.1955
[34 empty] | 8.4 | 0.0001-1.32039867109635i | 0.000000001 | 0.000192558139534884+0.161748837209302i | 2.30607627906977+0.0001i | 0.000192559139534884+0.161748837209302i | 0.000427881180278552+0.373005175911403i | 2.3062688382093+0.161848837209302i | 0.011479223199193+0.160929754083971i | 0.011579223199193-1.15946891701238i | 8.4 | 1.1595
CAPACITOR DESIGN RATINGS VS IEEE/ANSI MAXIMUMS | [33 empty] | 8.6 | 0.0001-1.2896917252569i | 0.000000001 | 0.000192558139534884+0.1656i | 2.30607627906977+0.0001i | 0.000192559139534884+0.1656i | 0.000427496063999482+0.381886251069868i | 2.3062688382093+0.1657i | 0.0120202911669125+0.164722552084812i | 0.0121202911669125-1.12496917317209i | 8.6 | 1.125
Capacitor Duty Rating: |  | HD- Heavy Duty Capacitors, with -40C to +55C Temperature Rating | [15 empty] | PowerFactory Input - HP Second Order | [7 empty] | 4.8 | [7 empty] | 8.8 | 0.0001-1.26038054968288i | 0.000000001 | 0.000192558139534884+0.169451162790698i | 2.30607627906977+0.0001i | 0.000192559139534884+0.169451162790698i | 0.000427110947720412+0.390767326228333i | 2.3062688382093+0.169551162790698i | 0.0125738258446611+0.168512626540711i | 0.0126738258446611-1.09186792314217i | 8.8 | 1.0919
|  | Capacitor Design Values |  |  |  |  | Capacitor Design Values
|  | At Nominal Voltage | At 110% System Voltage | Capacitor Rating |  |  | At Nominal Voltage | At 110% System Voltage |  | Capacitor Rating | [15 empty] | 6.7872 | [7 empty] | 9 | 0.0001-1.23237209302326i | 0.000000001 | 0.000192558139534884+0.173302325581395i | 2.30607627906977+0.0001i | 0.000192559139534884+0.173302325581395i | 0.000426725831441342+0.399648401386795i | 2.3062688382093+0.173402325581395i | 0.0131398089959597+0.172299916369567i | 0.0132398089959597-1.06007217665369i | 9 | 1.0602
% RATED VOLTS |  | 83.37% | 91.68% | 125% |  | % 60HZ AMPS: | 86.38% | 94.43% |  | 135% | [15 empty] | 216.3849 | [7 empty] | 9.2 | 0.0001-1.20558139534884i | 0.000000001 | 0.000192558139534884+0.177153488372093i | 2.30607627906977+0.0001i | 0.000192559139534884+0.177153488372093i | 0.000426340715162273+0.40852947654526i | 2.3062688382093+0.177253488372093i | 0.0137182219880368+0.176084360641551i | 0.0138182219880368-1.02949703470729i | 9.2 | 1.0296
% CREST VOLTAGE |  | 87.86% | 97.86% | 135% |  | % 60HZ KVAR: | 70.35% | 84.9% |  | 135% | [15 empty] | 2077.2947 | [7 empty] | 9.4 | 0.0001-1.17993072736269i | 0.000000001 | 0.000192558139534884+0.181004651162791i | 2.30607627906977+0.0001i | 0.000192559139534884+0.181004651162791i | 0.000425955598883203+0.417410551703725i | 2.3062688382093+0.181104651162791i | 0.014309045793349+0.179865898582289i | 0.014409045793349-1.0000648287804i | 9.4 | 1.0002
[34 empty] | 9.6 | 0.0001-1.1553488372093i | 0.000000001 | 0.000192558139534884+0.184855813953488i | 2.30607627906977+0.0001i | 0.000192559139534884+0.184855813953488i | 0.000425570482604133+0.426291626862187i | 2.3062688382093+0.184955813953488i | 0.0149122609911339+0.183644469576035i | 0.0150122609911339-0.971704367633265i | 9.6 | 0.97182
[34 empty] | 9.8 | 0.0001-1.13177028951115i | 0.000000001 | 0.000192558139534884+0.188706976744186i | 2.30607627906977+0.0001i | 0.000192559139534884+0.188706976744186i | 0.000425185366325063+0.435172702020652i | 2.3062688382093+0.188806976744186i | 0.0155278477689933+0.187420013168828i | 0.0156278477689933-0.944350276342322i | 9.8 | 0.94448
[34 empty] | 10 | 0.0001-1.10913488372093i | 0.000000001 | 0.000192558139534884+0.192558139534884i | 2.30607627906977+0.0001i | 0.000192559139534884+0.192558139534884i | 0.000424800250045994+0.444053777179117i | 2.3062688382093+0.192658139534884i | 0.0161557859245047+0.191192469071622i | 0.0162557859245047-0.917942414649308i | 10 | 0.91809
[34 empty] | 10.2 | 0.0001-1.08738714090287i | 0.000000001 | 0.000192558139534884+0.196409302325581i | 2.30607627906977+0.0001i | 0.000192559139534884+0.196409302325581i | 0.000424415133766924+0.452934852337579i | 2.3062688382093+0.196509302325581i | 0.0167960548668645+0.194961777163406i | 0.0168960548668645-0.892425363739464i | 10.2 | 0.89259
[34 empty] | 10.4 | 0.0001-1.06647584973166i | 0.000000001 | 0.000192558139534884+0.200260465116279i | 2.30607627906977+0.0001i | 0.000192559139534884+0.200260465116279i | 0.000424030017487854+0.461815927496044i | 2.3062688382093+0.200360465116279i | 0.0174486336185605+0.198727877494303i | 0.0175486336185605-0.867747972237357i | 10.4 | 0.86793
[34 empty] | 10.6 | 0.0001-1.04635366388767i | 0.000000001 | 0.000192558139534884+0.204111627906977i | 2.30607627906977+0.0001i | 0.000192559139534884+0.204111627906977i | 0.000423644901208784+0.470697002654509i | 2.3062688382093+0.204211627906977i | 0.0181135008170722+0.202490710288641i | 0.0182135008170722-0.843862953599029i | 10.6 | 0.84406
[34 empty] | 10.8 | 0.0001-1.02697674418605i | 0.000000001 | 0.000192558139534884+0.207962790697674i | 2.30607627906977+0.0001i | 0.000192559139534884+0.207962790697674i | 0.000423259784929715+0.479578077812971i | 2.3062688382093+0.208062790697674i | 0.0187906347166017+0.206250215948019i | 0.0188906347166017-0.820726528238031i | 10.8 | 0.82094
[34 empty] | 11 | 0.0001-1.0083044397463i | 0.000000001 | 0.000192558139534884+0.211813953488372i | 2.30607627906977+0.0001i | 0.000192559139534884+0.211813953488372i | 0.000422874668650645+0.488459152971436i | 2.3062688382093+0.211913953488372i | 0.0194800131898339+0.210006335054343i | 0.0195800131898339-0.798298104691957i | 11 | 0.79854
[34 empty] | 11.2 | 0.0001-0.99029900332226i | 0.000000001 | 0.000192558139534884+0.21566511627907i | 2.30607627906977+0.0001i | 0.000192559139534884+0.21566511627907i | 0.000422489552371575+0.497340228129901i | 2.3062688382093+0.21576511627907i | 0.0201816137297228+0.213759008372843i | 0.0202816137297228-0.776539994949417i | 11.2 | 0.7768
[34 empty] | 11.4 | 0.0001-0.972925336597308i | 0.000000001 | 0.000192558139534884+0.219516279069767i | 2.30607627906977+0.0001i | 0.000192559139534884+0.219516279069767i | 0.000422104436092505+0.506221303288363i | 2.3062688382093+0.219616279069767i | 0.0208954134513082+0.217508176855069i | 0.0209954134513082-0.755417159742239i | 11.4 | 0.75571
[34 empty] | 11.6 | 0.0001-0.956150761828389i | 0.000000001 | 0.000192558139534884+0.223367441860465i | 2.30607627906977+0.0001i | 0.000192559139534884+0.223367441860465i | 0.000421719319813435+0.515102378446828i | 2.3062688382093+0.223467441860465i | 0.0216213890935605+0.221253781641875i | 0.0217213890935605-0.734896980186514i | 11.6 | 0.73522
[34 empty] | 11.8 | 0.0001-0.939944816712654i | 0.000000001 | 0.000192558139534884+0.227218604651163i | 2.30607627906977+0.0001i | 0.000192559139534884+0.227218604651163i | 0.000421334203534366+0.523983453605293i | 2.3062688382093+0.227318604651163i | 0.0223595170212514+0.224995764066364i | 0.0224595170212514-0.71494905264629i | 11.8 | 0.7153
[34 empty] | 12 | 0.0001-0.924279069767443i | 0.000000001 | 0.000192558139534884+0.23106976744186i | 2.30607627906977+0.0001i | 0.000192559139534884+0.23106976744186i | 0.000420949087255296+0.532864528763756i | 2.3062688382093+0.23116976744186i | 0.0231097732268536+0.228734065656831i | 0.0232097732268536-0.695545004110612i | 12 | 0.69593
[34 empty] | 12.2 | 0.0001-0.909126953869616i | 0.000000001 | 0.000192558139534884+0.234920930232558i | 2.30607627906977+0.0001i | 0.000192559139534884+0.234920930232558i | 0.000420563970976226+0.54174560392222i | 2.3062688382093+0.235020930232558i | 0.0238721333324679+0.232468628139671i | 0.0239721333324679-0.676658325729945i | 12.2 | 0.67708
Northeast Power Systems, Inc. | [33 empty] | 12.4 | 0.0001-0.894463615903977i | 0.000000001 | 0.000192558139534884+0.238772093023256i | 2.30607627906977+0.0001i | 0.000192559139534884+0.238772093023256i | 0.000420178854697156+0.550626679080685i | 2.3062688382093+0.238872093023256i | 0.0246465725917754+0.236199393442267i | 0.0247465725917754-0.65826422246171i | 12.4 | 0.65873
High-Pass Design - Stage/Branch: Branch/Stage #, Tuning Point: 24.00, Reference: Enter Job Name | [9 empty] | Page 2 | [23 empty] | 12.6 | 0.0001-0.880265780730898i | 0.000000001 | 0.000192558139534884+0.242623255813953i | 2.30607627906977+0.0001i | 0.000192559139534884+0.242623255813953i | 0.000419793738418087+0.559507754239148i | 2.3062688382093+0.242723255813953i | 0.025433065892018+0.239926303695862i | 0.025533065892018-0.640339477035036i | 12.6 | 0.64085
[34 empty] | 12.8 | 0.0001-0.866511627906978i | 0.000000001 | 0.000192558139534884+0.246474418604651i | 2.30607627906977+0.0001i | 0.000192559139534884+0.246474418604651i | 0.000419408622139017+0.568388829397612i | 2.3062688382093+0.246574418604651i | 0.0262315877560053+0.243649301238402i | 0.0263315877560053-0.622862326668576i | 12.8 | 0.62342
[34 empty] | 13 | 0.0001-0.853180679785332i | 0.000000001 | 0.000192558139534884+0.250325581395349i | 2.30607627906977+0.0001i | 0.000192559139534884+0.250325581395349i | 0.000419023505859947+0.577269904556077i | 2.3062688382093+0.250425581395349i | 0.0270421123441456+0.24736832861736i | 0.0271421123441456-0.605812351167972i | 13 | 0.60642
[34 empty] | 13.2 | 0.0001-0.840253699788585i | 0.000000001 | 0.000192558139534884+0.254176744186046i | 2.30607627906977+0.0001i | 0.000192559139534884+0.254176744186046i | 0.000418638389580877+0.58615097971454i | 2.3062688382093+0.254276744186046i | 0.0278646134565048+0.25108332859253i | 0.0279646134565048-0.589170371196055i | 13.2 | 0.58983
[34 empty] | 13.4 | 0.0001-0.82771259979174i | 0.000000001 | 0.000192558139534884+0.258027906976744i | 2.30607627906977+0.0001i | 0.000192559139534884+0.258027906976744i | 0.000418253273301808+0.595032054873004i | 2.3062688382093+0.258127906976744i | 0.0286990645348896+0.254794244138807i | 0.0287990645348896-0.572918355652933i | 13.4 | 0.57364
[34 empty] | 13.6 | 0.0001-0.815540355677156i | 0.000000001 | 0.000192558139534884+0.261879069767442i | 2.30607627906977+0.0001i | 0.000192559139534884+0.261879069767442i | 0.000417868157022738+0.603913130031469i | 2.3062688382093+0.261979069767442i | 0.0295454386649558+0.258501018448938i | 0.0296454386649558-0.557039337228218i | 13.6 | 0.55783
[34 empty] | 13.8 | 0.0001-0.803720930232559i | 0.000000001 | 0.000192558139534884+0.265730232558139i | 2.30607627906977+0.0001i | 0.000192559139534884+0.265730232558139i | 0.000417483040743668+0.612794205189932i | 2.3062688382093+0.265830232558139i | 0.0304037085783418+0.262203594936248i | 0.0305037085783418-0.541517335296311i | 13.8 | 0.54238
[34 empty] | 14 | 0.0001-0.792239202657808i | 0.000000001 | 0.000192558139534884+0.269581395348837i | 2.30607627906977+0.0001i | 0.000192559139534884+0.269581395348837i | 0.000417097924464598+0.621675280348397i | 2.3062688382093+0.269681395348837i | 0.0312738466548267+0.265901917237345i | 0.0313738466548267-0.526337285420463i | 14 | 0.52727
[34 empty] | 14.2 | 0.0001-0.781080904028825i | 0.000000001 | 0.000192558139534884+0.273432558139535i | 2.30607627906977+0.0001i | 0.000192559139534884+0.273432558139535i | 0.000416712808185528+0.630556355506861i | 2.3062688382093+0.273532558139535i | 0.0321558249245114+0.2695959292148i | 0.0322558249245114-0.511484974814025i | 14.2 | 0.5125
Harmonic #: (n) |  | 1 | 2 | 3 | 4 | 5 | 7 | 11 | 13 | [24 empty] | 14.4 | 0.0001-0.770232558139536i | 0.000000001 | 0.000192558139534884+0.277283720930232i | 2.30607627906977+0.0001i | 0.000192559139534884+0.277283720930232i | 0.000416327691906459+0.639437430665324i | 2.3062688382093+0.277383720930232i | 0.0330496150700256+0.273285574959796i | 0.0331496150700256-0.49694698317974i | 14.4 | 0.49805
Filter Current (amps) (In) |  | 360.2245 | 0 | 0 | 0 | 100 | 0 | 0 | 0 | [24 empty] | 14.6 | 0.0001-0.759681427206118i | 0.000000001 | 0.000192558139534884+0.28113488372093i | 2.30607627906977+0.0001i | 0.000192559139534884+0.28113488372093i | 0.000415942575627389+0.648318505823789i | 2.3062688382093+0.28123488372093i | 0.0339551884287566+0.276970798794765i | 0.0340551884287566-0.482710628411353i | 14.6 | 0.48391
VCAP HARMONIC VOLTAGE (volts) |  | 3995.3757 | 0 | 0 | 0 | 221.827 | 0 | 0 | 0 | [24 empty] | 14.8 | 0.0001-0.749415461973603i | 0.000000001 | 0.000192558139534884+0.284986046511628i | 2.30607627906977+0.0001i | 0.000192559139534884+0.284986046511628i | 0.000415557459348319+0.657199580982254i | 2.3062688382093+0.285086046511628i | 0.0348725159951019+0.280651545275988i | 0.0349725159951019-0.468763916697615i | 14.8 | 0.47007
IREACTOR CURRENT (amps) |  | 360.212 | 0 | 0 | 0 | 99.913 | 0 | 0 | 0 | [24 empty] | 15 | 0.0001-0.739423255813955i | 0.000000001 | 0.000192558139534884+0.288837209302325i | 2.30607627906977+0.0001i | 0.000192559139534884+0.288837209302325i | 0.000415172343069249+0.666080656140716i | 2.3062688382093+0.288937209302325i | 0.0358015684227445+0.284327759196169i | 0.0359015684227445-0.455095496617786i | 15 | 0.45651
IRESISTOR CURRENT (amps) |  | 3.0078 | 0 | 0 | 0 | 4.1714 | 0 | 0 | 0 | [24 empty] | 15.2 | 0.0001-0.729694002447982i | 0.000000001 | 0.000192558139534884+0.292688372093023i | 2.30607627906977+0.0001i | 0.000192559139534884+0.292688372093023i | 0.00041478722679018+0.674961731299181i | 2.3062688382093+0.292788372093023i | 0.0367423160269525+0.287999385587i | 0.0368423160269525-0.441694616860982i | 15.2 | 0.44323
Filter Voltage Distortion |  | 100.1% | 0% | 0% | 0% | 5.327% | 0% | 0% | 0% | [24 empty] | 15.4 | 0.0001-0.720217456961644i | 0.000000001 | 0.000192558139534884+0.296539534883721i | 2.30607627906977+0.0001i | 0.000192559139534884+0.296539534883721i | 0.00041440211051111+0.683842806457646i | 2.3062688382093+0.296639534883721i | 0.0376947287868973+0.291666369721676i | 0.0377947287868973-0.428551087239968i | 15.4 | 0.43021
Harmonic #: (n) |  | 17 | 19 | 23 | 25 | 29 | 31 | 35 | 37 | [6 empty] | 1 | 2 | 3 | 4 | 5 | 7 | 11 | 13 | [10 empty] | 15.6 | 0.0001-0.71098389982111i | 0.000000001 | 0.000192558139534884+0.300390697674418i | 2.30607627906977+0.0001i | 0.000192559139534884+0.300390697674418i | 0.00041401699423204+0.692723881616108i | 2.3062688382093+0.300490697674418i | 0.0386587763479972+0.2953286571174i | 0.0387587763479972-0.41565524270371i | 15.6 | 0.41746
Filter Current (amps) (In) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | VCAP HARMONIC VOLTAGE (volts)^2 |  | 15963027.1643 | 0 | 0 | 0 | 49207.2076 | 0 | 0 | 0 | [10 empty] | 15.8 | 0.0001-0.701984103620843i | 0.000000001 | 0.000192558139534884+0.304241860465116i | 2.30607627906977+0.0001i | 0.000192559139534884+0.304241860465116i | 0.00041363187795297+0.701604956774573i | 2.3062688382093+0.304341860465116i | 0.0396344280242816+0.298986193537865i | 0.0397344280242816-0.402997910082978i | 15.8 | 0.40495
VCAP HARMONIC VOLTAGE (volts) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | Filter Current (amps) (In)^2 |  | 129761.6991 | 0 | 0 | 0 | 10000 | 0 | 0 | 0 | [10 empty] | 16 | 0.0001-0.693209302325583i | 0.000000001 | 0.000192558139534884+0.308093023255814i | 2.30607627906977+0.0001i | 0.000192559139534884+0.308093023255814i | 0.000413246761673901+0.710486031933038i | 2.3062688382093+0.308193023255814i | 0.040621652800775+0.302638924995689i | 0.040721652800775-0.390570377329894i | 16 | 0.39269
IREACTOR CURRENT (amps) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | kvar (single phase) |  | 1439.2323 | 0 | 0 | 0 | 22.1827 | 0 | 0 | 0 | [10 empty] | 16.2 | 0.0001-0.684651162790699i | 0.000000001 | 0.000192558139534884+0.311944186046511i | 2.30607627906977+0.0001i | 0.000192559139534884+0.311944186046511i | 0.000412861645394831+0.7193671070915i | 2.3062688382093+0.312044186046511i | 0.0416204193359034+0.306286797754845i | 0.0417204193359034-0.378364365035854i | 16.2 | 0.38066
IRESISTOR CURRENT (amps) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [24 empty] | 16.4 | 0.0001-0.676301758366422i | 0.000000001 | 0.000192558139534884+0.315795348837209i | 2.30607627906977+0.0001i | 0.000192559139534884+0.315795348837209i | 0.000412476529115761+0.728248182249965i | 2.3062688382093+0.315895348837209i | 0.0426306959639222+0.309929758333057i | 0.0427306959639222-0.366372000033365i | 16.4 | 0.36886
Filter Voltage Distortion |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | [24 empty] | 16.6 | 0.0001-0.6681535444102i | 0.000000001 | 0.000192558139534884+0.319646511627907i | 2.30607627906977+0.0001i | 0.000192559139534884+0.319646511627907i | 0.000412091412836691+0.73712925740843i | 2.3062688382093+0.319746511627907i | 0.0436524506973609+0.31356775350416i | 0.0437524506973609-0.35458579090604i | 16.6 | 0.35727
System Voltage Distortion (Vthd %) |  | 5.327% | [13 empty] | 17 | 19 | 23 | 25 | 29 | 31 | 35 | 37 | [10 empty] | 16.8 | 0.0001-0.660199335548174i | 0.000000001 | 0.000192558139534884+0.323497674418604i | 2.30607627906977+0.0001i | 0.000192559139534884+0.323497674418604i | 0.000411706296557622+0.746010332566892i | 2.3062688382093+0.323597674418604i | 0.0446856512294911+0.317200730300445i | 0.0447856512294911-0.342998605247729i | 16.8 | 0.34591
FILTER ONE-LINE DIAGRAM | [13 empty] | VCAP HARMONIC VOLTAGE (volts)^2 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 17 | 0.0001-0.652432284541725i | 0.000000001 | 0.000192558139534884+0.327348837209302i | 2.30607627906977+0.0001i | 0.000192559139534884+0.327348837209302i | 0.000411321180278552+0.754891407725357i | 2.3062688382093+0.327448837209302i | 0.0457302649368132+0.320828636014972i | 0.0458302649368132-0.331603648526753i | 17 | 0.33476
Filter Bank Fundamental amps 360.2 amps/phase | [7 empty] | Reactor Fundamental Design Margin: | 1.5 |  |  |  |  | Filter Current (amps) (In)^2 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 17.2 | 0.0001-0.644845862628449i | 0.000000001 | 0.000192558139534884+0.331199999999999i | 2.30607627906977+0.0001i | 0.000192559139534884+0.331199999999999i | 0.000410936063999482+0.763772482883819i | 2.3062688382093+0.331299999999999i | 0.0467862588815602+0.324451418203852i | 0.0468862588815602-0.320394444424597i | 17.2 | 0.32381
Filter Bank RMS AMPS 373.85 amps/phase | [7 empty] | Reactor Harmonic Design Margin: | 1.5 |  |  |  |  | kvar (single phase) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 17.4 | 0.0001-0.637433841218927i | 0.000000001 | 0.000192558139534884+0.335051162790697i | 2.30607627906977+0.0001i | 0.000192559139534884+0.335051162790697i | 0.000410550947720412+0.772653558042284i | 2.3062688382093+0.335151162790697i | 0.0478535998142244+0.328069024688509i | 0.0479535998142244-0.309364816530418i | 17.4 | 0.31306
[34 empty] | 17.6 | 0.0001-0.630190274841439i | 0.000000001 | 0.000192558139534884+0.338902325581395i | 2.30607627906977+0.0001i | 0.000192559139534884+0.338902325581395i | 0.000410165831441342+0.781534633200749i | 2.3062688382093+0.339002325581395i | 0.0489322541760978+0.331681403557902i | 0.0490322541760978-0.298508871283537i | 17.6 | 0.30251
High-Pass Resistor: 2.3 ohms/Phase | [5 empty] | Reference: High-Pass Filter Design - Stage/Branch: Branch/Stage #, Tuning Point: 24.00, Reference: Enter Job Name | [27 empty] | 17.8 | 0.0001-0.623109485236479i | 0.000000001 | 0.000192558139534884+0.342753488372092i | 2.30607627906977+0.0001i | 0.000192559139534884+0.342753488372092i | 0.000409780715162273+0.790415708359212i | 2.3062688382093+0.342853488372092i | 0.0500221881018341+0.335288503170729i | 0.0501221881018341-0.28782098206575i | 17.8 | 0.29215
0 KW/Phase Total | [33 empty] | 18 | 0.0001-0.616186046511629i | 0.000000001 | 0.000192558139534884+0.34660465116279i | 2.30607627906977+0.0001i | 0.000192559139534884+0.34660465116279i | 0.000409395598883203+0.799296783517676i | 2.3062688382093+0.34670465116279i | 0.0511233674220285+0.338890272157606i | 0.0512233674220285-0.277295774354023i | 18 | 0.28199
5.14 RMS Amps | [5 empty] | Current Ratings |  |  | Design & Construction Details | [24 empty] | 18.2 | 0.0001-0.609414771275238i | 0.000000001 | 0.000192558139534884+0.350455813953488i | 2.30607627906977+0.0001i | 0.000192559139534884+0.350455813953488i | 0.000409010482604133+0.808177858676141i | 2.3062688382093+0.350555813953488i | 0.0522357576658119+0.342486659423199i | 0.0523357576658119-0.266928111852039i | 18.2 | 0.27201
[6 empty] | Harm # | Amps |  | Quantity: | 3 |  |  |  | harmonic # |  | 1 | 2 | 3 | 4 | 5 | 7 | 11 | 13 | 17 | 19 | 23 | 25 | 29 | 31 | 35 | 37 |  |  | 18.4 | 0.0001-0.60279069767442i | 0.000000001 | 0.000192558139534884+0.354306976744185i | 2.30607627906977+0.0001i | 0.000192559139534884+0.354306976744185i | 0.000408625366325063+0.817058933834604i | 2.3062688382093+0.354406976744185i | 0.0533593240634654+0.346077614148348i | 0.0534593240634654-0.256713083526072i | 18.4 | 0.26222
Iron-Core Filter Reactor: 0.02 ohms, 0.05 mH | [5 empty] | 1 | 540.3368 |  | Number of Phases: | 3 |  |  |  | Total filter amps |  | 360.2245 | 0 | 0 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 18.6 | 0.0001-0.596309077269319i | 0.000000001 | 0.000192558139534884+0.358158139534883i | 2.30607627906977+0.0001i | 0.000192559139534884+0.358158139534883i | 0.000408240250045994+0.825940008993069i | 2.3062688382093+0.358258139534883i | 0.0544940315490504+0.349663085792154i | 0.0545940315490504-0.246645991477165i | 18.6 | 0.25262 |  |  |  | 540.3368 | 291963.8229
I1= 360.2 amps nominal | [5 empty] | 2 | 0 |  | System Voltage: | 6.9 kV |  |  |  | R & X EQUIVALENT IMPEDANCE (ohms) |  | 0.019255 | 0.038506 | 0.057749 | 0.07698 | 0.096195 | 0.13456 | 0.21093 | 0.24886 | 0.3241 | 0.36134 | 0.43494 | 0.47124 | 0.54273 | 0.57788 | 0.64689 | 0.68072 |  |  | 18.8 | 0.0001-0.589965363681347i | 0.000000001 | 0.000192558139534884+0.362009302325581i | 2.30607627906977+0.0001i | 0.000192559139534884+0.362009302325581i | 0.000407855133766924+0.834821084151533i | 2.3062688382093+0.362109302325581i | 0.0556398447630542+0.353243024094031i | 0.0557398447630542-0.236722339587316i | 18.8 | 0.2432 |  |  |  | 0 | 0
[6 empty] | 3 | 0 |  | BIL Rating (kV): | 95 |  |  |  | I REACTOR (Calculate voltage then divide by xLn) |  | 360.212 | 0 | 0 | 0 | 99.913 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 19 | 0.0001-0.583755201958386i | 0.000000001 | 0.000192558139534884+0.365860465116278i | 2.30607627906977+0.0001i | 0.000192559139534884+0.365860465116278i | 0.000407470017487854+0.843702159309996i | 2.3062688382093+0.365960465116278i | 0.0567967280550526+0.356817379075737i | 0.0568967280550526-0.226937822882649i | 19 | 0.23396 |  |  |  | 0 | 0
[6 empty] | 4 | 0 |  | Fundamental Frequency: | 60 |  |  |  | I RESISTOR (calculate voltage then divide by R) |  | 3.0078 | 0 | 0 | 0 | 4.1714 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 19.2 | 0.0001-0.577674418604652i | 0.000000001 | 0.000192558139534884+0.369711627906976i | 2.30607627906977+0.0001i | 0.000192559139534884+0.369711627906976i | 0.000407084901208784+0.852583234468461i | 2.3062688382093+0.369811627906976i | 0.0579646454863889+0.360386101043377i | 0.0580646454863889-0.217288317561275i | 19.2 | 0.22491 |  |  |  | 0 | 0
[6 empty] | 5 | 150 |  | Inductance (mH): | 0.051079 |  |  |  | Resistor losses (watts) |  | 20.8625 | 0 | 0 | 0 | 40.1267 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 19.4 | 0.0001-0.571719012227285i | 0.000000001 | 0.000192558139534884+0.373562790697674i | 2.30607627906977+0.0001i | 0.000192559139534884+0.373562790697674i | 0.000406699784929715+0.861464309626925i | 2.3062688382093+0.373662790697674i | 0.0591435608328655+0.36394914058937i | 0.0592435608328655-0.207769871637915i | 19.4 | 0.21605 |  |  |  | 150 | 22500
[6 empty] | 7 | 0 |  | Reactance at 60Hz (ohms): | 0.019256 |  |  |  | I Resistor ^2 (watts) |  | 9.0468 | 0 | 0 | 0 | 17.4004 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Resistor RMS Amps | 5.1427 | 19.6 | 0.0001-0.565885144755578i | 0.000000001 | 0.000192558139534884+0.377413953488371i | 2.30607627906977+0.0001i | 0.000192559139534884+0.377413953488371i | 0.000406314668650645+0.870345384785388i | 2.3062688382093+0.377513953488371i | 0.0603334375874531+0.367506448594388i | 0.0604334375874531-0.19837869616119i | 19.6 | 0.20738 |  |  |  | 0 | 0
Main Capacitor Fuse: 324 (Minimum Amps) | [5 empty] | 11 | 0 |  | Taps: | None |  |  |  | Total filter amps^2 |  | 129761.6991 | 0 | 0 | 0 | 10000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Total Filter RMS Amps | 373.8472 | 19.8 | 0.0001-0.56016913319239i | 0.000000001 | 0.000192558139534884+0.381265116279069i | 2.30607627906977+0.0001i | 0.000192559139534884+0.381265116279069i | 0.000405929552371575+0.879226459943853i | 2.3062688382093+0.381365116279069i | 0.0615342389630142+0.371057976229273i | 0.0616342389630142-0.189111156963117i | 19.8 | 0.1989 |  |  |  | 0 | 0
[6 empty] | 13 | 0 |  | Insulation Type: | Nomex |  |  |  | I2R REACTOR LOSSES (watts) |  | 24.9849 | 0 | 0 | 0 | 1.9222 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 20 | 0.0001-0.554567441860466i | 0.000000001 | 0.000192558139534884+0.385116279069767i | 2.30607627906977+0.0001i | 0.000192559139534884+0.385116279069767i | 0.000405544436092505+0.888107535102317i | 2.3062688382093+0.385216279069767i | 0.0627459278950383+0.374603674956911i | 0.0628459278950383-0.179963766903555i | 20 | 0.19062 |  |  |  | 0 | 0
[6 empty] | 17 | 0 |  | Ambient: | 60C | [23 empty] | 20.2 | 0.0001-0.549076675109373i | 0.000000001 | 0.000192558139534884+0.388967441860464i | 2.30607627906977+0.0001i | 0.000192559139534884+0.388967441860464i | 0.000405159319813436+0.89698861026078i | 2.3062688382093+0.389067441860464i | 0.0639684670443937+0.378143496534092i | 0.0640684670443937-0.170933178575281i | 20.2 | 0.18255 |  |  |  | 0 | 0
Main Capacitor: Qty(6), 1039 kvar, 4.8 kV, 119.58 µF/Can | [5 empty] | 19 | 0 |  | Temperature Rise: | 115C Rise over Ambient | [23 empty] | 20.4 | 0.0001-0.543693570451438i | 0.000000001 | 0.000192558139534884+0.392818604651162i | 2.30607627906977+0.0001i | 0.000192559139534884+0.392818604651162i | 0.000404774203534366+0.905869685419245i | 2.3062688382093+0.392918604651162i | 0.0652018188000927+0.381677393013325i | 0.0653018188000927-0.162016177438113i | 20.4 | 0.17468 |  |  |  | 0 | 0
[6 empty] | 23 | 0 |  | Winding Type: | CU/AL - Based On Price |  |  |  |  | Reactor Current Squared | 129752.6523 | 0 | 0 | 0 | 9982.5996 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 373.8118 |  | 20.6 | 0.0001-0.53841499209754i | 0.000000001 | 0.000192558139534884+0.39666976744186i | 2.30607627906977+0.0001i | 0.000192559139534884+0.39666976744186i | 0.000404389087255296+0.914750760577709i | 2.3062688382093+0.39676976744186i | 0.0664459452820669+0.385205316744632i | 0.0665459452820669-0.153209675352908i | 20.6 | 0.16704 |  |  |  | 0 | 0
[6 empty] | 25 | 0 |  | Tack Winding to Core: | Yes | [23 empty] | 20.8 | 0.0001-0.533237924865833i | 0.000000001 | 0.000192558139534884+0.400520930232557i | 2.30607627906977+0.0001i | 0.000192559139534884+0.400520930232557i | 0.000404003970976226+0.923631835736172i | 2.3062688382093+0.400620930232557i | 0.0677008083439587+0.388727220377314i | 0.0678008083439587-0.144510704488519i | 20.8 | 0.15963 |  |  |  | 0 | 0
[6 empty] | 29 | 0 |  | Enclosure: | None/Open Construction | [23 empty] | 21 | 0.0001-0.528159468438539i | 0.000000001 | 0.000192558139534884+0.404372093023255i | 2.30607627906977+0.0001i | 0.000192559139534884+0.404372093023255i | 0.000403618854697156+0.932512910894637i | 2.3062688382093+0.404472093023255i | 0.0689663695759242+0.392243056861678i | 0.0690663695759242-0.135916411576861i | 21 | 0.15246 |  |  |  | 0 | 0
6.9kV, 60Hz High-Pass Harmonic Filter, Wye-Connected | [5 empty] | 31 | 0 | [26 empty] | 21.2 | 0.0001-0.523176831943836i | 0.000000001 | 0.000192558139534884+0.408223255813953i | 2.30607627906977+0.0001i | 0.000192559139534884+0.408223255813953i | 0.000403233738418087+0.941393986053102i | 2.3062688382093+0.408323255813953i | 0.0702425903074461+0.39575277945074i | 0.0703425903074461-0.127424052493096i | 21.2 | 0.14555 |  |  |  | 0 | 0
4.30 MVAR 3-Phase, 24.0 Tuning | [5 empty] | 35 | 0 | [26 empty] | 21.4 | 0.0001-0.518287328841557i | 0.000000001 | 0.000192558139534884+0.41207441860465i | 2.30607627906977+0.0001i | 0.000192559139534884+0.41207441860465i | 0.000402848622139017+0.950275061211564i | 2.3062688382093+0.41217441860465i | 0.0715294316101608+0.399256341701895i | 0.0716294316101608-0.119030987139662i | 21.4 | 0.13892 |  |  |  | 0 | 0
[6 empty] | 37 | 0 | [26 empty] | 21.6 | 0.0001-0.513488372093024i | 0.000000001 | 0.000192558139534884+0.415925581395348i | 2.30607627906977+0.0001i | 0.000192559139534884+0.415925581395348i | 0.000402463505859947+0.959156136370029i | 2.3062688382093+0.416025581395348i | 0.0728268543006966+0.402753697478564i | 0.0729268543006966-0.11073467461446i | 21.6 | 0.13259 |  |  |  | 0 | 0
[6 empty] | RMS: | 560.7707 | [26 empty] | 21.8 | 0.0001-0.508777469596758i | 0.000000001 | 0.000192558139534884+0.419776744186046i | 2.30607627906977+0.0001i | 0.000192559139534884+0.419776744186046i | 0.000402078389580877+0.968037211528494i | 2.3062688382093+0.419876744186046i | 0.0741348189435203+0.406244800951796i | 0.0742348189435203-0.102532668644962i | 21.8 | 0.12658 |  |  |  |  | 314463.8229
[34 empty] | 22 | 0.0001-0.504152219873151i | 0.000000001 | 0.000192558139534884+0.423627906976743i | 2.30607627906977+0.0001i | 0.000192559139534884+0.423627906976743i | 0.000401693273301808+0.976918286686956i | 2.3062688382093+0.423727906976743i | 0.0754532858537964+0.409729606601853i | 0.0755532858537964-0.094422613271298i | 22 | 0.12093 |  |  |  |  | 560.7707 | reactor RMS amps (for supplier with margin)
Where: | [33 empty] | 22.2 | 0.0001-0.499610307982402i | 0.000000001 | 0.000192558139534884+0.427479069767441i | 2.30607627906977+0.0001i | 0.000192559139534884+0.427479069767441i | 0.000401308157022738+0.985799361845421i | 2.3062688382093+0.427579069767441i | 0.0767822151002582+0.413208069219762i | 0.0768822151002582-0.08640223876264i | 22.2 | 0.11566
Xeff | Effective reactance of the harmonic filter | [32 empty] | 22.4 | 0.0001-0.495149501661131i | 0.000000001 | 0.000192558139534884+0.431330232558139i | 2.30607627906977+0.0001i | 0.000192559139534884+0.431330232558139i | 0.000400923040743668+0.994680437003886i | 2.3062688382093+0.431430232558139i | 0.0781215665080835+0.416680143908828i | 0.0782215665080835-0.078469357752303i | 22.4 | 0.1108
Qeff | Effective Reactive Power (MVAR) of the harmonic filter (fundamental current only, not including harmonics) | [32 empty] | 22.6 | 0.0001-0.49076764766413i | 0.000000001 | 0.000192558139534884+0.435181395348836i | 2.30607627906977+0.0001i | 0.000192559139534884+0.435181395348836i | 0.000400537924464598+1.00356151216235i | 2.3062688382093+0.435281395348836i | 0.0794712996617846+0.420145786086126i | 0.0795712996617846-0.070621861578004i | 22.6 | 0.10639
QFILTER | Kvar rating of harmonic filter. Includes reactive power associated with fundamental and harmonic current. | [32 empty] | 22.8 | 0.0001-0.486462668298655i | 0.000000001 | 0.000192558139534884+0.439032558139534i | 2.30607627906977+0.0001i | 0.000192559139534884+0.439032558139534i | 0.000400152808185529+1.01244258732081i | 2.3062688382093+0.439132558139534i | 0.0808313739081057+0.423604951483956i | 0.0809313739081057-0.062857716814699i | 22.8 | 0.10247
QRATED PER PHASE | kvar rating of capacitors at their rated voltage (not the application voltage) | [32 empty] | 23 | 0.0001-0.482232558139536i | 0.000000001 | 0.000192558139534884+0.442883720930232i | 2.30607627906977+0.0001i | 0.000192559139534884+0.442883720930232i | 0.000399767691906459+1.02132366247928i | 2.3062688382093+0.442983720930232i | 0.0822017483589293+0.427057596151281i | 0.0823017483589293-0.055174961988255i | 23 | 0.099085
VLLSYS | Nominal System Line-to-Line Voltage | [32 empty] | 23.2 | 0.0001-0.478075380914195i | 0.000000001 | 0.000192558139534884+0.446734883720929i | 2.30607627906977+0.0001i | 0.000192559139534884+0.446734883720929i | 0.000399382575627389+1.03020473763774i | 2.3062688382093+0.446834883720929i | 0.0835823818941875+0.430503676455099i | 0.0836823818941875-0.047571704459096i | 23.2 | 0.096259
XC | Capacitive reactance of the harmonic filter capacitor at fundamental frequency | [32 empty] | 23.4 | 0.0001-0.473989266547407i | 0.000000001 | 0.000192558139534884+0.450586046511627i | 2.30607627906977+0.0001i | 0.000192559139534884+0.450586046511627i | 0.000398997459348319+1.03908581279621i | 2.3062688382093+0.450686046511627i | 0.0849732331647901+0.43394314908184i | 0.0850732331647901-0.040046117465567i | 23.4 | 0.094027
XL | Inductive Reactance of the harmonic filter reactor at fundamental frequency | [32 empty] | 23.6 | 0.0001-0.469972408356327i | 0.000000001 | 0.000192558139534884+0.454437209302325i | 2.30607627906977+0.0001i | 0.000192559139534884+0.454437209302325i | 0.000398612343069249+1.04796688795467i | 2.3062688382093+0.454537209302325i | 0.0863742605955476+0.43737597103867i | 0.0864742605955476-0.032596437317657i | 23.6 | 0.092414
h | harmonic number of tuning filter tuning point | [32 empty] | 23.8 | 0.0001-0.466023060386947i | 0.000000001 | 0.000192558139534884+0.458288372093022i | 2.30607627906977+0.0001i | 0.000192559139534884+0.458288372093022i | 0.00039822722679018+1.05684796311313i | 2.3062688382093+0.458388372093022i | 0.0877854223881145+0.440802099654821i | 0.0878854223881145-0.025220960732126i | 23.8 | 0.091433
f | frequency | [32 empty] | 24 | 0.0001-0.462139534883722i | 0.000000001 | 0.000192558139534884+0.46213953488372i | 2.30607627906977+0.0001i | 0.000192559139534884+0.46213953488372i | 0.00039784211051111+1.0657290382716i | 2.3062688382093+0.46223953488372i | 0.0892066765239316+0.444221492582852i | 0.0893066765239316-0.01791804230087i | 24 | 0.091086
H | Reactor Henry Rating (milliHenrys) | [32 empty] | 24.2 | 0.0001-0.458320199884683i | 0.000000001 | 0.000192558139534884+0.465990697674418i | 2.30607627906977+0.0001i | 0.000192559139534884+0.465990697674418i | 0.00039745699423204+1.07461011343006i | 2.3062688382093+0.466090697674418i | 0.0906379807671727+0.447634107799881i | 0.0907379807671727-0.010686092084802i | 24.2 | 0.091365
IRATED FUNDAMENTAL | Fundamental Current Rating of Filter Bank | [32 empty] | 24.4 | 0.0001-0.454563476934809i | 0.000000001 | 0.000192558139534884+0.469841860465115i | 2.30607627906977+0.0001i | 0.000192559139534884+0.469841860465115i | 0.00039707187795297+1.08349118858852i | 2.3062688382093+0.469941860465115i | 0.0920792926677073+0.451039903608819i | 0.0921792926677073-0.00352357332598996i | 24.4 | 0.092247
VCAP FUNDAMENTAL VOLTAGE | Fundamental Voltage Drop Across Capacitor | [32 empty] | 24.6 | 0.0001-0.450867838910948i | 0.000000001 | 0.000192558139534884+0.473693023255813i | 2.30607627906977+0.0001i | 0.000192559139534884+0.473693023255813i | 0.000396686761673901+1.09237226374699i | 2.3062688382093+0.473793023255813i | 0.0935305695640614+0.45443883863954i | 0.0936305695640614+0.00357099972859198i | 24.6 | 0.093699
VCAP HARMONIC VOLTAGE | Harmonic Voltage Drop Across Capacitor | [32 empty] | 24.8 | 0.0001-0.447231807951989i | 0.000000001 | 0.000192558139534884+0.477544186046511i | 2.30607627906977+0.0001i | 0.000192559139534884+0.477544186046511i | 0.000396301645394831+1.10125333890545i | 2.3062688382093+0.477644186046511i | 0.0949917685863814+0.457830871850017i | 0.0950917685863814+0.0105990638980279i | 24.8 | 0.095681
VCAP RMS VOLTAGE | Capacitor RMS Voltage (Fundamental Voltage + Harmonic Voltages) | [32 empty] | 25 | 0.0001-0.443653953488373i | 0.000000001 | 0.000192558139534884+0.481395348837208i | 2.30607627906977+0.0001i | 0.000192559139534884+0.481395348837208i | 0.000395916529115761+1.11013441406392i | 2.3062688382093+0.481495348837208i | 0.0964628466594143+0.461215962527471i | 0.0965628466594143+0.017562009039098i | 25 | 0.098147
VPEAK CAP VOLTAGE | Capacitor Voltage assuming or harmonics are coincident | [32 empty] | 25.2 | 0.0001-0.44013289036545i | 0.000000001 | 0.000192558139534884+0.485246511627906i | 2.30607627906977+0.0001i | 0.000192559139534884+0.485246511627906i | 0.000395531412836691+1.11901548922238i | 2.3062688382093+0.485346511627906i | 0.0979437605054787+0.464594070289427i | 0.0980437605054787+0.024461179923977i | 25.2 | 0.10105
N | Number of Capacitors per phase | [32 empty] | 25.4 | 0.0001-0.436667277055485i | 0.000000001 | 0.000192558139534884+0.489097674418604i | 2.30607627906977+0.0001i | 0.000192559139534884+0.489097674418604i | 0.000395146296557622+1.12789656438085i | 2.3062688382093+0.489197674418604i | 0.0994344666474536+0.467965155084802i | 0.0995344666474536+0.031297878029317i | 25.4 | 0.10434
VCAP var rating | Capacitor Can Var Rating (in Kvar) | [32 empty] | 25.6 | 0.0001-0.433255813953489i | 0.000000001 | 0.000192558139534884+0.492948837209301i | 2.30607627906977+0.0001i | 0.000192559139534884+0.492948837209301i | 0.000394761180278552+1.13677763953931i | 2.3062688382093+0.493048837209301i | 0.100934921411758+0.471329177194902i | 0.101034921411758+0.038073363241413i | 25.6 | 0.10797
ICAP RMS CURRENT | RMS Current Seen By Capacitor (amps) | [32 empty] | 25.8 | 0.0001-0.4298972417523i | 0.000000001 | 0.000192558139534884+0.496799999999999i | 2.30607627906977+0.0001i | 0.000192559139534884+0.496799999999999i | 0.000394376063999482+1.14565871469777i | 2.3062688382093+0.496899999999999i | 0.102445080931346+0.474686097234442i | 0.102545080931346+0.044788855482142i | 25.8 | 0.1119
IFILTER RMS CURRENT | RMS Current into Filter Branch (amps) | [32 empty] | 26 | 0.0001-0.426590339892667i | 0.000000001 | 0.000192558139534884+0.500651162790697i | 2.30607627906977+0.0001i | 0.000192559139534884+0.500651162790697i | 0.000393990947720412+1.15453978985624i | 2.3062688382093+0.500751162790697i | 0.1039649011487+0.478035876152508i | 0.1040649011487+0.051445536259841i | 26 | 0.11609
DF | Damping Factor is defined as the resistance of the resistor to the reactance of the reactor at the filter tuned frequency | [32 empty] | 26.2 | 0.0001-0.423333925084326i | 0.000000001 | 0.000192558139534884+0.504502325581394i | 2.30607627906977+0.0001i | 0.000192559139534884+0.504502325581394i | 0.000393605831441343+1.1634208650147i | 2.3062688382093+0.504602325581394i | 0.105494337818822+0.481378475233467i | 0.105594337818822+0.058044550149141i | 26.2 | 0.1205
* Formulas taken From IEEE Std. 1531-2003 - IEEE Guide for Application and Specification of Harmonic Filters | [33 empty] | 26.4 | 0.0001-0.420126849894293i | 0.000000001 | 0.000192558139534884+0.508353488372092i | 2.30607627906977+0.0001i | 0.000192559139534884+0.508353488372092i | 0.000393220715162273+1.17230194017317i | 2.3062688382093+0.508453488372092i | 0.107033346512239+0.484713856097913i | 0.107133346512239+0.06458700620362i | 26.4 | 0.1251
[34 empty] | 26.6 | 0.0001-0.416968001398847i | 0.000000001 | 0.000192558139534884+0.51220465116279i | 2.30607627906977+0.0001i | 0.000192559139534884+0.51220465116279i | 0.000392835598883203+1.18118301533163i | 2.3062688382093+0.51230465116279i | 0.108581882617996+0.488041980703496i | 0.108681882617996+0.071073979304649i | 26.6 | 0.12986
[34 empty] | 26.8 | 0.0001-0.413856299895871i | 0.000000001 | 0.000192558139534884+0.516055813953487i | 2.30607627906977+0.0001i | 0.000192559139534884+0.516055813953487i | 0.000392450482604133+1.19006409049009i | 2.3062688382093+0.516155813953487i | 0.11013990134667+0.491362811345804i | 0.11023990134667+0.077506511449933i | 26.8 | 0.13476
[34 empty] | 27 | 0.0001-0.41079069767442i | 0.000000001 | 0.000192558139534884+0.519906976744185i | 2.30607627906977+0.0001i | 0.000192559139534884+0.519906976744185i | 0.000392065366325063+1.19894516564856i | 2.3062688382093+0.520006976744185i | 0.111707357733365+0.494676310659155i | 0.111807357733365+0.083885612984735i | 27 | 0.13978
[34 empty] | 27.2 | 0.0001-0.407770177838578i | 0.000000001 | 0.000192558139534884+0.523758139534883i | 2.30607627906977+0.0001i | 0.000192559139534884+0.523758139534883i | 0.000391680250045994+1.20782624080702i | 2.3062688382093+0.523858139534883i | 0.113284206640722+0.497982441617372i | 0.113384206640722+0.090212263778794i | 27.2 | 0.14489
[34 empty] | 27.4 | 0.0001-0.404793753182822i | 0.000000001 | 0.000192558139534884+0.52760930232558i | 2.30607627906977+0.0001i | 0.000192559139534884+0.52760930232558i | 0.000391295133766924+1.21670731596548i | 2.3062688382093+0.52770930232558i | 0.114870402761926+0.501281167534558i | 0.114970402761926+0.096487414351736i | 27.4 | 0.15009
Northeast Power Systems, Inc. | [33 empty] | 27.6 | 0.0001-0.40186046511628i | 0.000000001 | 0.000192558139534884+0.531460465116278i | 2.30607627906977+0.0001i | 0.000192559139534884+0.531460465116278i | 0.000390910017487854+1.22558839112395i | 2.3062688382093+0.531560465116278i | 0.116465900623712+0.504572452065806i | 0.116565900623712+0.102711986949526i | 27.6 | 0.15536
High-Pass Filter Design - Stage/Branch: Branch/Stage #, Tuning Point: 24.00, Reference: Enter Job Name | [9 empty] | Page 3 | [23 empty] | 27.8 | 0.0001-0.398969382633429i | 0.000000001 | 0.000192558139534884+0.535311627906976i | 2.30607627906977+0.0001i | 0.000192559139534884+0.535311627906976i | 0.000390524901208784+1.23446946628241i | 2.3062688382093+0.535411627906976i | 0.118070654589373+0.507856259207877i | 0.118170654589373+0.108886876574448i | 27.8 | 0.16069
[34 empty] | 28 | 0.0001-0.396119601328905i | 0.000000001 | 0.000192558139534884+0.539162790697673i | 2.30607627906977+0.0001i | 0.000192559139534884+0.539162790697673i | 0.000390139784929715+1.24335054144088i | 2.3062688382093+0.539262790697673i | 0.11968461886177+0.511132553299892i | 0.11978461886177+0.115012951970987i | 28 | 0.16606
[34 empty] | 28.2 | 0.0001-0.393310242454232i | 0.000000001 | 0.000192558139534884+0.543013953488371i | 2.30607627906977+0.0001i | 0.000192559139534884+0.543013953488371i | 0.000389754668650645+1.25223161659934i | 2.3062688382093+0.543113953488371i | 0.121307747486332+0.514401299023928i | 0.121407747486332+0.121091056569696i | 28.2 | 0.17147
[34 empty] | 28.4 | 0.0001-0.390540452014413i | 0.000000001 | 0.000192558139534884+0.546865116279069i | 2.30607627906977+0.0001i | 0.000192559139534884+0.546865116279069i | 0.000389369552371575+1.26111269175781i | 2.3062688382093+0.546965116279069i | 0.122939994354073+0.517662461405655i | 0.123039994354073+0.127122009391242i | 28.4 | 0.17691
[34 empty] | 28.6 | 0.0001-0.387809399902424i | 0.000000001 | 0.000192558139534884+0.550716279069766i | 2.30607627906977+0.0001i | 0.000192559139534884+0.550716279069766i | 0.000388984436092505+1.26999376691627i | 2.3062688382093+0.550816279069766i | 0.124581313204584+0.520916005814873i | 0.124681313204584+0.133106605912449i | 28.6 | 0.18238
[34 empty] | 28.8 | 0.0001-0.385116279069768i | 0.000000001 | 0.000192558139534884+0.554567441860464i | 2.30607627906977+0.0001i | 0.000192559139534884+0.554567441860464i | 0.000388599319813436+1.27887484207473i | 2.3062688382093+0.554667441860464i | 0.126231657629051+0.524161897966082i | 0.126331657629051+0.139045618896314i | 28.8 | 0.18787
[34 empty] | 29 | 0.0001-0.382460304731356i | 0.000000001 | 0.000192558139534884+0.558418604651162i | 2.30607627906977+0.0001i | 0.000192559139534884+0.558418604651162i | 0.000388214203534366+1.2877559172332i | 2.3062688382093+0.558518604651162i | 0.127890981073247+0.527400103918985i | 0.127990981073247+0.144939799187629i | 29 | 0.19336
[34 empty] | 29.2 | 0.0001-0.379840713603059i | 0.000000001 | 0.000192558139534884+0.562269767441859i | 2.30607627906977+0.0001i | 0.000192559139534884+0.562269767441859i | 0.000387829087255296+1.29663699239166i | 2.3062688382093+0.562369767441859i | 0.12955923684053+0.530630590078955i | 0.12965923684053+0.150789876475896i | 29.2 | 0.19887
[34 empty] | 29.4 | 0.0001-0.377256763170385i | 0.000000001 | 0.000192558139534884+0.566120930232557i | 2.30607627906977+0.0001i | 0.000192559139534884+0.566120930232557i | 0.000387443970976226+1.30551806755013i | 2.3062688382093+0.566220930232557i | 0.131236378094854+0.533853323197516i | 0.131336378094854+0.156596560027131i | 29.4 | 0.20438
[34 empty] | 29.6 | 0.0001-0.374707730986802i | 0.000000001 | 0.000192558139534884+0.569972093023254i | 2.30607627906977+0.0001i | 0.000192559139534884+0.569972093023254i | 0.000387058854697157+1.31439914270859i | 2.3062688382093+0.570072093023254i | 0.132922357863747+0.53706827037274i | 0.133022357863747+0.162360539385938i | 29.6 | 0.20989
[34 empty] | 29.8 | 0.0001-0.372192914000313i | 0.000000001 | 0.000192558139534884+0.573823255813952i | 2.30607627906977+0.0001i | 0.000192559139534884+0.573823255813952i | 0.000386673738418087+1.32328021786705i | 2.3062688382093+0.573923255813952i | 0.134617129041314+0.540275399049663i | 0.134717129041314+0.16808248504935i | 29.8 | 0.21541
[34 empty] | 30 | 0.0001-0.369711627906978i | 0.000000001 | 0.000192558139534884+0.57767441860465i | 2.30607627906977+0.0001i | 0.000192559139534884+0.57767441860465i | 0.000386288622139017+1.33216129302552i | 2.3062688382093+0.57777441860465i | 0.136320644391224+0.543474677020642i | 0.136420644391224+0.173763049113664i | 30 | 0.22092
[34 empty] | 30.2 | 0.0001-0.36726320653011i | 0.000000001 | 0.000192558139534884+0.581525581395347i | 2.30607627906977+0.0001i | 0.000192559139534884+0.581525581395347i | 0.000385903505859947+1.34104236818398i | 2.3062688382093+0.581625581395347i | 0.138032856549686+0.546666072425678i | 0.138132856549686+0.179402865895568i | 30.2 | 0.22642
[34 empty] | 30.4 | 0.0001-0.364847001223991i | 0.000000001 | 0.000192558139534884+0.585376744186045i | 2.30607627906977+0.0001i | 0.000192559139534884+0.585376744186045i | 0.000385518389580877+1.34992344334245i | 2.3062688382093+0.585476744186045i | 0.139753718028445+0.549849553752752i | 0.139853718028445+0.185002552528761i | 30.4 | 0.23192
[34 empty] | 30.6 | 0.0001-0.362462380300959i | 0.000000001 | 0.000192558139534884+0.589227906976743i | 2.30607627906977+0.0001i | 0.000192559139534884+0.589227906976743i | 0.000385133273301808+1.35880451850091i | 2.3062688382093+0.589327906976743i | 0.141483181217742+0.553025089838073i | 0.141583181217742+0.190562709537114i | 30.6 | 0.2374
[34 empty] | 30.8 | 0.0001-0.360108728480822i | 0.000000001 | 0.000192558139534884+0.593079069767441i | 2.30607627906977+0.0001i | 0.000192559139534884+0.593079069767441i | 0.000384748157022738+1.36768559365937i | 2.3062688382093+0.593179069767441i | 0.1432211983893+0.556192649866353i | 0.1433211983893+0.196083921385531i | 30.8 | 0.24288
[34 empty] | 31 | 0.0001-0.357785446361591i | 0.000000001 | 0.000192558139534884+0.596930232558138i | 2.30607627906977+0.0001i | 0.000192559139534884+0.596930232558138i | 0.000384363040743668+1.37656666881784i | 2.3062688382093+0.597030232558138i | 0.144967721699281+0.55935220337102i | 0.145067721699281+0.201566757009429i | 31 | 0.24834
[34 empty] | 31.2 | 0.0001-0.355491949910556i | 0.000000001 | 0.000192558139534884+0.600781395348836i | 2.30607627906977+0.0001i | 0.000192559139534884+0.600781395348836i | 0.000383977924464598+1.3854477439763i | 2.3062688382093+0.600881395348836i | 0.146722703191253+0.562503720234395i | 0.146822703191253+0.207011770323839i | 31.2 | 0.25379
[34 empty] | 31.4 | 0.0001-0.35322766997482i | 0.000000001 | 0.000192558139534884+0.604632558139533i | 2.30607627906977+0.0001i | 0.000192559139534884+0.604632558139533i | 0.000383592808185529+1.39432881913476i | 2.3062688382093+0.604732558139533i | 0.148486094799144+0.565647170687884i | 0.148586094799144+0.212419500713064i | 31.4 | 0.25923
[34 empty] | 31.6 | 0.0001-0.350992051810422i | 0.000000001 | 0.000192558139534884+0.608483720930231i | 2.30607627906977+0.0001i | 0.000192559139534884+0.608483720930231i | 0.000383207691906459+1.40320989429323i | 2.3062688382093+0.608583720930231i | 0.150257848350198+0.568782525312103i | 0.150357848350198+0.217790473501681i | 31.6 | 0.26465
[34 empty] | 31.8 | 0.0001-0.348784554629224i | 0.000000001 | 0.000192558139534884+0.612334883720929i | 2.30607627906977+0.0001i | 0.000192559139534884+0.612334883720929i | 0.000382822575627389+1.41209096945169i | 2.3062688382093+0.612434883720929i | 0.152037915567907+0.571909755036974i | 0.152137915567907+0.22312520040775i | 31.8 | 0.27006
[34 empty] | 32 | 0.0001-0.346604651162792i | 0.000000001 | 0.000192558139534884+0.616186046511626i | 2.30607627906977+0.0001i | 0.000192559139534884+0.616186046511626i | 0.000382437459348319+1.42097204461016i | 2.3062688382093+0.616286046511626i | 0.153826248074967+0.575028831141831i | 0.153926248074967+0.228424179979039i | 32 | 0.27545
[34 empty] | 32.2 | 0.0001-0.344451827242526i | 0.000000001 | 0.000192558139534884+0.620037209302324i | 2.30607627906977+0.0001i | 0.000192559139534884+0.620037209302324i | 0.00038205234306925+1.42985311976862i | 2.3062688382093+0.620137209302324i | 0.155622797396191+0.578139725255448i | 0.155722797396191+0.233687898012922i | 32.2 | 0.28082
[34 empty] | 32.4 | 0.0001-0.34232558139535i | 0.000000001 | 0.000192558139534884+0.623888372093022i | 2.30607627906977+0.0001i | 0.000192559139534884+0.623888372093022i | 0.00038166722679018+1.43873419492709i | 2.3062688382093+0.623988372093022i | 0.157427514961451+0.58124240935609i | 0.157527514961451+0.23891682796074i | 32.4 | 0.28618
[34 empty] | 32.6 | 0.0001-0.340225424454274i | 0.000000001 | 0.000192558139534884+0.62773953488372i | 2.30607627906977+0.0001i | 0.000192559139534884+0.62773953488372i | 0.00038128211051111+1.44761527008555i | 2.3062688382093+0.62783953488372i | 0.159240352108581+0.584336855771486i | 0.159340352108581+0.244111431317212i | 32.6 | 0.29151
[34 empty] | 32.8 | 0.0001-0.338150879183211i | 0.000000001 | 0.000192558139534884+0.631590697674417i | 2.30607627906977+0.0001i | 0.000192559139534884+0.631590697674417i | 0.00038089699423204+1.45649634524401i | 2.3062688382093+0.631690697674417i | 0.161061260086295+0.587423037178821i | 0.161161260086295+0.24927215799561i | 32.8 | 0.29683
[34 empty] | 33 | 0.0001-0.336101479915434i | 0.000000001 | 0.000192558139534884+0.635441860465115i | 2.30607627906977+0.0001i | 0.000192559139534884+0.635441860465115i | 0.00038051187795297+1.46537742040248i | 2.3062688382093+0.635541860465115i | 0.162890190057092+0.590500926604675i | 0.162990190057092+0.254399446689241i | 33 | 0.30213
[34 empty] | 33.2 | 0.0001-0.3340767722051i | 0.000000001 | 0.000192558139534884+0.639293023255813i | 2.30607627906977+0.0001i | 0.000192559139534884+0.639293023255813i | 0.000380126761673901+1.47425849556094i | 2.3062688382093+0.639393023255813i | 0.16472709310014+0.593570497424926i | 0.16482709310014+0.259493725219826i | 33.2 | 0.30742
Filter Losses | [33 empty] | 33.4 | 0.0001-0.332076312491297i | 0.000000001 | 0.000192558139534884+0.64314418604651i | 2.30607627906977+0.0001i | 0.000192559139534884+0.64314418604651i | 0.000379741645394831+1.48313957071941i | 2.3062688382093+0.64324418604651i | 0.16657192021417+0.596631723364667i | 0.16667192021417+0.26455541087337i | 33.4 | 0.31268
[34 empty] | 33.6 | 0.0001-0.330099667774087i | 0.000000001 | 0.000192558139534884+0.646995348837208i | 2.30607627906977+0.0001i | 0.000192559139534884+0.646995348837208i | 0.000379356529115761+1.49202064587787i | 2.3062688382093+0.647095348837208i | 0.168424622320352+0.599684578498039i | 0.168524622320352+0.269584910723952i | 33.6 | 0.31793
Main Capacitor Losses |  | 311.5942 | Watts, 3-Phase or 1063 BTUs/Hour | [30 empty] | 33.8 | 0.0001-0.328146415302051i | 0.000000001 | 0.000192558139534884+0.650846511627906i | 2.30607627906977+0.0001i | 0.000192559139534884+0.650846511627906i | 0.000378971412836691+1.50090172103634i | 2.3062688382093+0.650946511627906i | 0.170285150265164+0.602729037248105i | 0.170385150265164+0.274582621946054i | 33.8 | 0.32315
Main Capacitor Fuse Losses |  | 3567.3823 | Watts, 3-Phase or 12172 BTUs/Hour | [30 empty] | 34 | 0.0001-0.326216142270862i | 0.000000001 | 0.000192558139534884+0.654697674418604i | 2.30607627906977+0.0001i | 0.000192559139534884+0.654697674418604i | 0.000378586296557622+1.5097827961948i | 2.3062688382093+0.654797674418604i | 0.172153454823249+0.605765074386624i | 0.172253454823249+0.279548932115762i | 34 | 0.32836
[34 empty] | 34.2 | 0.0001-0.324308445532436i | 0.000000001 | 0.000192558139534884+0.658548837209301i | 2.30607627906977+0.0001i | 0.000192559139534884+0.658548837209301i | 0.000378201180278552+1.51866387135326i | 2.3062688382093+0.658648837209301i | 0.174029486700267+0.608792665033866i | 0.174129486700267+0.28448421950143i | 34.2 | 0.33355
High Pass Resistor Losses, 60 Hertz |  | 62.5875 | Watts, 3-Phase or 214 BTUs/Hour | [30 empty] | 34.4 | 0.0001-0.322422931314224i | 0.000000001 | 0.000192558139534884+0.662399999999999i | 2.30607627906977+0.0001i | 0.000192559139534884+0.662399999999999i | 0.000377816063999482+1.52754494651173i | 2.3062688382093+0.662499999999999i | 0.17591319653574+0.611811784658364i | 0.17601319653574+0.28938885334414i | 34.4 | 0.33871
High Pass Resistor Losses, (harmonic) |  | 120.3802 | Watts, 3-Phase or 411 BTUs/Hour | [30 empty] | 34.6 | 0.0001-0.320559214948246i | 0.000000001 | 0.000192558139534884+0.666251162790697i | 2.30607627906977+0.0001i | 0.000192559139534884+0.666251162790697i | 0.000377430947720412+1.53642602167019i | 2.3062688382093+0.666351162790697i | 0.177804534905872+0.61482240907663i | 0.177904534905872+0.294263194128384i | 34.6 | 0.34386
Iron-Core Reactor Losses, 60 Hertz |  | 74.9548 | Watts, 3-Phase or 256 BTUs/Hour | [30 empty] | 34.8 | 0.0001-0.318716920609463i | 0.000000001 | 0.000192558139534884+0.670102325581395i | 2.30607627906977+0.0001i | 0.000192559139534884+0.670102325581395i | 0.000377045831441342+1.54530709682866i | 2.3062688382093+0.670202325581395i | 0.179703452326384+0.617824514452899i | 0.179803452326384+0.299107593843436i | 34.8 | 0.34899
Iron-Core Reactor Losses, (harmonic) |  | 5.7667 | Watts, 3-Phase or 20 BTUs/Hour | [30 empty] | 35 | 0.0001-0.316895681063123i | 0.000000001 | 0.000192558139534884+0.673953488372092i | 2.30607627906977+0.0001i | 0.000192559139534884+0.673953488372092i | 0.000376660715162273+1.55418817198712i | 2.3062688382093+0.674053488372092i | 0.181609899255312+0.620818077298773i | 0.181709899255312+0.30392239623565i | 35 | 0.3541
[34 empty] | 35.2 | 0.0001-0.315095137420719i | 0.000000001 | 0.000192558139534884+0.67780465116279i | 2.30607627906977+0.0001i | 0.000192559139534884+0.67780465116279i | 0.000376275598883203+1.56306924714558i | 2.3062688382093+0.67790465116279i | 0.183523826095815+0.623803074472914i | 0.183623826095815+0.308707937052195i | 35.2 | 0.35919
Total 60 Hz Losses |  | 4016.5187 | Watts, 3-Phase or 13705 BTUs/Hour | [30 empty] | 35.4 | 0.0001-0.313314938904218i | 0.000000001 | 0.000192558139534884+0.681655813953488i | 2.30607627906977+0.0001i | 0.000192559139534884+0.681655813953488i | 0.000375890482604133+1.57195032230405i | 2.3062688382093+0.681755813953488i | 0.185445183198962+0.626779483180661i | 0.185545183198962+0.313464544276443i | 35.4 | 0.36426
Total Harmonic Losses |  | 126.1469 | Watts, 3-Phase or 430 BTUs/Hour | [30 empty] | 35.6 | 0.0001-0.311554742618239i | 0.000000001 | 0.000192558139534884+0.685506976744185i | 2.30607627906977+0.0001i | 0.000192559139534884+0.685506976744185i | 0.000375505366325063+1.58083139746251i | 2.3062688382093+0.685606976744185i | 0.187373920866509+0.62974728097363i | 0.187473920866509+0.318192538355391i | 35.6 | 0.36931
Total Harmonic Losses |  | 4142.6656 | Watts, 3-Phase or 14135 BTUs/Hour | [30 empty] | 35.8 | 0.0001-0.309814213329869i | 0.000000001 | 0.000192558139534884+0.689358139534883i | 2.30607627906977+0.0001i | 0.000192559139534884+0.689358139534883i | 0.000375120250045994+1.58971247262098i | 2.3062688382093+0.689458139534883i | 0.18930998935367+0.632706445749324i | 0.18940998935367+0.322892232419455i | 35.8 | 0.37435
[34 empty] | 36 | 0.0001-0.308093023255814i | 0.000000001 | 0.000192558139534884+0.693209302325581i | 2.30607627906977+0.0001i | 0.000192559139534884+0.693209302325581i | 0.000374735133766924+1.59859354777944i | 2.3062688382093+0.693309302325581i | 0.191253338871864+0.635656955750666i | 0.191353338871864+0.327563932494852i | 36 | 0.37936
[34 empty] | 36.2 | 0.0001-0.306390851856611i | 0.000000001 | 0.000192558139534884+0.697060465116279i | 2.30607627906977+0.0001i | 0.000192559139534884+0.697060465116279i | 0.000374350017487854+1.60747462293791i | 2.3062688382093+0.697160465116279i | 0.193203919591472+0.638598789565561i | 0.193303919591472+0.33220793770895i | 36.2 | 0.38435
[34 empty] | 36.4 | 0.0001-0.304707385637618i | 0.000000001 | 0.000192558139534884+0.700911627906976i | 2.30607627906977+0.0001i | 0.000192559139534884+0.700911627906976i | 0.000373964901208784+1.61635569809637i | 2.3062688382093+0.701011627906976i | 0.195161681644554+0.641531926126379i | 0.195261681644554+0.336824540488761i | 36.4 | 0.38933
[34 empty] | 36.6 | 0.0001-0.303042317956539i | 0.000000001 | 0.000192558139534884+0.704762790697674i | 2.30607627906977+0.0001i | 0.000192559139534884+0.704762790697674i | 0.000373579784929715+1.62523677325483i | 2.3062688382093+0.704862790697674i | 0.197126575127584+0.644456344709472i | 0.197226575127584+0.341414026752933i | 36.6 | 0.39429
[34 empty] | 36.8 | 0.0001-0.301395348837209i | 0.000000001 | 0.000192558139534884+0.708613953488372i | 2.30607627906977+0.0001i | 0.000192559139534884+0.708613953488372i | 0.000373194668650645+1.6341178484133i | 2.3062688382093+0.708713953488372i | 0.199098550104146+0.647372024934629i | 0.199198550104146+0.34597667609742i | 36.8 | 0.39922
[34 empty] | 37 | 0.0001-0.299766184789441i | 0.000000001 | 0.000192558139534884+0.71246511627907i | 2.30607627906977+0.0001i | 0.000192559139534884+0.71246511627907i | 0.000372809552371575+1.64299892357176i | 2.3062688382093+0.71256511627907i | 0.201077556607632+0.6502789467645i | 0.201177556607632+0.350512761975059i | 37 | 0.40414
[34 empty] | 37.2 | 0.0001-0.298154538634659i | 0.000000001 | 0.000192558139534884+0.716316279069767i | 2.30607627906977+0.0001i | 0.000192559139534884+0.716316279069767i | 0.000372424436092505+1.65187999873023i | 2.3062688382093+0.716416279069767i | 0.203063544643931+0.653177090504051i | 0.203163544643931+0.355022551869392i | 37.2 | 0.40904
[34 empty] | 37.4 | 0.0001-0.296560129337147i | 0.000000001 | 0.000192558139534884+0.720167441860465i | 2.30607627906977+0.0001i | 0.000192559139534884+0.720167441860465i | 0.000372039319813435+1.66076107388869i | 2.3062688382093+0.720267441860465i | 0.205056464194086+0.656066436799919i | 0.205156464194086+0.359506307462772i | 37.4 | 0.41393
[34 empty] | 37.6 | 0.0001-0.294982681840673i | 0.000000001 | 0.000192558139534884+0.724018604651163i | 2.30607627906977+0.0001i | 0.000192559139534884+0.724018604651163i | 0.000371654203534366+1.66964214904715i | 2.3062688382093+0.724118604651163i | 0.207056265216961+0.658946966639821i | 0.207156265216961+0.363964284799148i | 37.6 | 0.41879
[34 empty] | 37.8 | 0.0001-0.293421926910299i | 0.000000001 | 0.000192558139534884+0.72786976744186i | 2.30607627906977+0.0001i | 0.000192559139534884+0.72786976744186i | 0.000371269087255296+1.67852322420562i | 2.3062688382093+0.72796976744186i | 0.209062897651881+0.661818661351891i | 0.209162897651881+0.368396734441592i | 37.8 | 0.42363
[34 empty] | 38 | 0.0001-0.291877600979192i | 0.000000001 | 0.000192558139534884+0.731720930232558i | 2.30607627906977+0.0001i | 0.000192559139534884+0.731720930232558i | 0.000370883970976226+1.68740429936408i | 2.3062688382093+0.731820930232558i | 0.211076311421256+0.664681502603992i | 0.211176311421256+0.3728039016248i | 38 | 0.42846
[34 empty] | 38.2 | 0.0001-0.290349446000244i | 0.000000001 | 0.000192558139534884+0.735572093023256i | 2.30607627906977+0.0001i | 0.000192559139534884+0.735572093023256i | 0.000370498854697156+1.69628537452255i | 2.3062688382093+0.735672093023256i | 0.213096456433203+0.667535472403058i | 0.213196456433203+0.377186026402814i | 38.2 | 0.43327
[34 empty] | 38.4 | 0.0001-0.288837209302326i | 0.000000001 | 0.000192558139534884+0.739423255813954i | 2.30607627906977+0.0001i | 0.000192559139534884+0.739423255813954i | 0.000370113738418087+1.70516644968101i | 2.3062688382093+0.739523255813954i | 0.215123282584144+0.670380553094343i | 0.215223282584144+0.381543343792017i | 38.4 | 0.43806
[34 empty] | 38.6 | 0.0001-0.287340643451018i | 0.000000001 | 0.000192558139534884+0.743274418604651i | 2.30607627906977+0.0001i | 0.000192559139534884+0.743274418604651i | 0.000369728622139017+1.71404752483947i | 2.3062688382093+0.743374418604651i | 0.217156739761397+0.673216727360714i | 0.217256739761397+0.385876083909696i | 38.6 | 0.44283
[34 empty] | 38.8 | 0.0001-0.285859506113642i | 0.000000001 | 0.000192558139534884+0.747125581395349i | 2.30607627906977+0.0001i | 0.000192559139534884+0.747125581395349i | 0.000369343505859947+1.72292859999794i | 2.3062688382093+0.747225581395349i | 0.219196777845745+0.676043978221879i | 0.219296777845745+0.390184472108237i | 38.8 | 0.44759
[34 empty] | 39 | 0.0001-0.284393559928444i | 0.000000001 | 0.000192558139534884+0.750976744186047i | 2.30607627906977+0.0001i | 0.000192559139534884+0.750976744186047i | 0.000368958389580877+1.7318096751564i | 2.3062688382093+0.751076744186047i | 0.221243346713996+0.6788622890336i | 0.221343346713996+0.394468729105156i | 39 | 0.45233
[34 empty] | 39.2 | 0.0001-0.282942572377788i | 0.000000001 | 0.000192558139534884+0.754827906976745i | 2.30607627906977+0.0001i | 0.000192559139534884+0.754827906976745i | 0.000368573273301807+1.74069075031487i | 2.3062688382093+0.754927906976745i | 0.223296396241531+0.681671643486919i | 0.223396396241531+0.398729071109131i | 39.2 | 0.45705
[34 empty] | 39.4 | 0.0001-0.281506315665211i | 0.000000001 | 0.000192558139534884+0.758679069767442i | 2.30607627906977+0.0001i | 0.000192559139534884+0.758679069767442i | 0.000368188157022738+1.74957182547333i | 2.3062688382093+0.758779069767442i | 0.225355876304826+0.684472025607306i | 0.225455876304826+0.402965709942095i | 39.4 | 0.46175
[34 empty] | 39.6 | 0.0001-0.280084566596194i | 0.000000001 | 0.000192558139534884+0.76253023255814i | 2.30607627906977+0.0001i | 0.000192559139534884+0.76253023255814i | 0.000367803040743668+1.7584529006318i | 2.3062688382093+0.76263023255814i | 0.227421736783977+0.687263419753849i | 0.227521736783977+0.407178853157655i | 39.6 | 0.46643
[34 empty] | 39.8 | 0.0001-0.278677106462545i | 0.000000001 | 0.000192558139534884+0.766381395348838i | 2.30607627906977+0.0001i | 0.000192559139534884+0.766381395348838i | 0.000367417924464598+1.76733397579026i | 2.3062688382093+0.766481395348838i | 0.229493927565185+0.690045810618365i | 0.229593927565185+0.41136870415582i | 39.8 | 0.4711
[34 empty] | 40 | 0.0001-0.277283720930232i | 0.000000001 | 0.000192558139534884+0.770232558139536i | 2.30607627906977+0.0001i | 0.000192559139534884+0.770232558139536i | 0.000367032808185528+1.77621505094873i | 2.3062688382093+0.770332558139536i | 0.231572398543256+0.692819183224548i | 0.231672398543256+0.415535462294316i | 40 | 0.47575
[34 empty] | 40.2 | 0.0001-0.27590419993058i | 0.000000001 | 0.000192558139534884+0.774083720930233i | 2.30607627906977+0.0001i | 0.000192559139534884+0.774083720930233i | 0.000366647691906459+1.78509612610719i | 2.3062688382093+0.774183720930233i | 0.233657099624054+0.695583522927039i | 0.233757099624054+0.419679322996459i | 40.2 | 0.48039
[34 empty] | 40.4 | 0.0001-0.274538337554686i | 0.000000001 | 0.000192558139534884+0.777934883720931i | 2.30607627906977+0.0001i | 0.000192559139534884+0.777934883720931i | 0.000366262575627389+1.79397720126565i | 2.3062688382093+0.778034883720931i | 0.235747980726967+0.698338815410529i | 0.235847980726967+0.423800477855843i | 40.4 | 0.48501
[34 empty] | 40.6 | 0.0001-0.273185931950968i | 0.000000001 | 0.000192558139534884+0.781786046511629i | 2.30607627906977+0.0001i | 0.000192559139534884+0.781786046511629i | 0.000365877459348319+1.80285827642412i | 2.3062688382093+0.781886046511629i | 0.237844991787339+0.701085046688815i | 0.237944991787339+0.427899114737847i | 40.6 | 0.48961
[34 empty] | 40.8 | 0.0001-0.271846785225718i | 0.000000001 | 0.000192558139534884+0.785637209302327i | 2.30607627906977+0.0001i | 0.000192559139534884+0.785637209302327i | 0.000365492343069249+1.81173935158258i | 2.3062688382093+0.785737209302327i | 0.239948082758886+0.703822203103825i | 0.240048082758886+0.431975417878107i | 40.8 | 0.49419
[34 empty] | 41 | 0.0001-0.270520703346568i | 0.000000001 | 0.000192558139534884+0.789488372093024i | 2.30607627906977+0.0001i | 0.000192559139534884+0.789488372093024i | 0.00036510722679018+1.82062042674104i | 2.3062688382093+0.789588372093024i | 0.24205720361611+0.706550271324667i | 0.24215720361611+0.436029567978099i | 41 | 0.49876
[34 empty] | 41.2 | 0.0001-0.269207496048769i | 0.000000001 | 0.000192558139534884+0.793339534883722i | 2.30607627906977+0.0001i | 0.000192559139534884+0.793339534883722i | 0.00036472211051111+1.82950150189951i | 2.3062688382093+0.793439534883722i | 0.244172304356687+0.70926923834662i | 0.244272304356687+0.440061742297851i | 41.2 | 0.50331
[34 empty] | 41.4 | 0.0001-0.267906976744186i | 0.000000001 | 0.000192558139534884+0.79719069767442i | 2.30607627906977+0.0001i | 0.000192559139534884+0.79719069767442i | 0.00036433699423204+1.83838257705797i | 2.3062688382093+0.79729069767442i | 0.246293335003831+0.711979091490109i | 0.246393335003831+0.444072114745923i | 41.4 | 0.50785
[34 empty] | 41.6 | 0.0001-0.266618962432916i | 0.000000001 | 0.000192558139534884+0.801041860465117i | 2.30607627906977+0.0001i | 0.000192559139534884+0.801041860465117i | 0.00036395187795297+1.84726365221644i | 2.3062688382093+0.801141860465117i | 0.248420245608664+0.714679818399702i | 0.248520245608664+0.448060855966786i | 41.6 | 0.51237
[34 empty] | 41.8 | 0.0001-0.265343273617447i | 0.000000001 | 0.000192558139534884+0.804893023255815i | 2.30607627906977+0.0001i | 0.000192559139534884+0.804893023255815i | 0.0003635667616739+1.8561447273749i | 2.3062688382093+0.804993023255815i | 0.250552986252541+0.717371407043028i | 0.250652986252541+0.452028133425581i | 41.8 | 0.51687
[34 empty] | 42 | 0.0001-0.264079734219269i | 0.000000001 | 0.000192558139534884+0.808744186046513i | 2.30607627906977+0.0001i | 0.000192559139534884+0.808744186046513i | 0.000363181645394831+1.86502580253337i | 2.3062688382093+0.808844186046513i | 0.252691507049389+0.72005384570974i | 0.252791507049389+0.455974111490471i | 42 | 0.52136
[34 empty] | 42.2 | 0.0001-0.26282817149785i | 0.000000001 | 0.000192558139534884+0.812595348837211i | 2.30607627906977+0.0001i | 0.000192559139534884+0.812595348837211i | 0.000362796529115761+1.87390687769183i | 2.3062688382093+0.812695348837211i | 0.254835758147997+0.722727123010401i | 0.254935758147997+0.459898951512551i | 42.2 | 0.52583
[34 empty] | 42.4 | 0.0001-0.261588415971917i | 0.000000001 | 0.000192558139534884+0.816446511627908i | 2.30607627906977+0.0001i | 0.000192559139534884+0.816446511627908i | 0.000362411412836691+1.88278795285029i | 2.3062688382093+0.816546511627908i | 0.256985689734321+0.72539122787541i | 0.257085689734321+0.463802811903493i | 42.4 | 0.53029
[34 empty] | 42.6 | 0.0001-0.260360301342941i | 0.000000001 | 0.000192558139534884+0.820297674418606i | 2.30607627906977+0.0001i | 0.000192559139534884+0.820297674418606i | 0.000362026296557621+1.89166902800876i | 2.3062688382093+0.820397674418606i | 0.259141252033746+0.728046149553866i | 0.259241252033746+0.467685848210925i | 42.6 | 0.53473
[34 empty] | 42.8 | 0.0001-0.259143664420778i | 0.000000001 | 0.000192558139534884+0.824148837209304i | 2.30607627906977+0.0001i | 0.000192559139534884+0.824148837209304i | 0.000361641180278552+1.90055010316722i | 2.3062688382093+0.824248837209304i | 0.261302395313342+0.730691877612431i | 0.261402395313342+0.471548213191653i | 42.8 | 0.53916
[34 empty] | 43 | 0.0001-0.257938345051379i | 0.000000001 | 0.000192558139534884+0.828000000000002i | 2.30607627906977+0.0001i | 0.000192559139534884+0.828000000000002i | 0.000361256063999482+1.90943117832569i | 2.3062688382093+0.828100000000002i | 0.263469069884109+0.733328401934195i | 0.263569069884109+0.475390056882816i | 43 | 0.54357
[34 empty] | 43.2 | 0.0001-0.256744186046511i | 0.000000001 | 0.000192558139534884+0.831851162790699i | 2.30607627906977+0.0001i | 0.000192559139534884+0.831851162790699i | 0.000360870947720412+1.91831225348415i | 2.3062688382093+0.831951162790699i | 0.265641226103187+0.735955712717487i | 0.265741226103187+0.479211526670976i | 43.2 | 0.54796
[34 empty] | 43.4 | 0.0001-0.255561033115421i | 0.000000001 | 0.000192558139534884+0.835702325581397i | 2.30607627906977+0.0001i | 0.000192559139534884+0.835702325581397i | 0.000360485831441342+1.92719332864262i | 2.3062688382093+0.835802325581397i | 0.267818814376073+0.738573800474714i | 0.267918814376073+0.483012767359293i | 43.4 | 0.55234
[34 empty] | 43.6 | 0.0001-0.254388734798378i | 0.000000001 | 0.000192558139534884+0.839553488372095i | 2.30607627906977+0.0001i | 0.000192559139534884+0.839553488372095i | 0.000360100715162272+1.93607440380108i | 2.3062688382093+0.839653488372095i | 0.27000178515879+0.741182656031135i | 0.27010178515879+0.486793921232757i | 43.6 | 0.55671
[34 empty] | 43.8 | 0.0001-0.253227142402038i | 0.000000001 | 0.000192558139534884+0.843404651162792i | 2.30607627906977+0.0001i | 0.000192559139534884+0.843404651162792i | 0.000359715598883203+1.94495547895954i | 2.3062688382093+0.843504651162792i | 0.272190088960069+0.743782270523674i | 0.272290088960069+0.490555128121636i | 43.8 | 0.56106
[34 empty] | 44 | 0.0001-0.252076109936575i | 0.000000001 | 0.000192558139534884+0.84725581395349i | 2.30607627906977+0.0001i | 0.000192559139534884+0.84725581395349i | 0.000359330482604133+1.95383655411801i | 2.3062688382093+0.84735581395349i | 0.274383676343494+0.746372635399673i | 0.274483676343494+0.494296525463098i | 44 | 0.56539
[34 empty] | 44.2 | 0.0001-0.250935494054509i | 0.000000001 | 0.000192558139534884+0.851106976744188i | 2.30607627906977+0.0001i | 0.000192559139534884+0.851106976744188i | 0.000358945366325063+1.96271762927647i | 2.3062688382093+0.851206976744188i | 0.276582497929629+0.748953742415644i | 0.276682497929629+0.498018248361135i | 44.2 | 0.56972
[34 empty] | 44.4 | 0.0001-0.2498051539912i | 0.000000001 | 0.000192558139534884+0.854958139534886i | 2.30607627906977+0.0001i | 0.000192559139534884+0.854958139534886i | 0.000358560250045993+1.97159870443494i | 2.3062688382093+0.855058139534886i | 0.278786504398143+0.751525583636028i | 0.278886504398143+0.501720429644828i | 44.4 | 0.57402
[34 empty] | 44.6 | 0.0001-0.248684951506935i | 0.000000001 | 0.000192558139534884+0.858809302325583i | 2.30607627906977+0.0001i | 0.000192559139534884+0.858809302325583i | 0.000358175133766924+1.9804797795934i | 2.3062688382093+0.858909302325583i | 0.280995646489897+0.754088151431896i | 0.281095646489897+0.505403199924961i | 44.6 | 0.57831
[34 empty] | 44.8 | 0.0001-0.247574750830564i | 0.000000001 | 0.000192558139534884+0.862660465116281i | 2.30607627906977+0.0001i | 0.000192559139534884+0.862660465116281i | 0.000357790017487854+1.98936085475186i | 2.3062688382093+0.862760465116281i | 0.283209875009027+0.756641438479681i | 0.283309875009027+0.509066687649117i | 44.8 | 0.58259
[34 empty] | 45 | 0.0001-0.246474418604651i | 0.000000001 | 0.000192558139534884+0.866511627906979i | 2.30607627906977+0.0001i | 0.000192559139534884+0.866511627906979i | 0.000357404901208784+1.99824192991033i | 2.3062688382093+0.866611627906979i | 0.285429140825006+0.759185437759873i | 0.285529140825006+0.512711019155222i | 45 | 0.58686
[34 empty] | 45.2 | 0.0001-0.245383823832064i | 0.000000001 | 0.000192558139534884+0.870362790697677i | 2.30607627906977+0.0001i | 0.000192559139534884+0.870362790697677i | 0.000357019784929714+2.00712300506879i | 2.3062688382093+0.870462790697677i | 0.287653394874677+0.761720142555683i | 0.287753394874677+0.516336318723619i | 45.2 | 0.59111
[34 empty] | 45.4 | 0.0001-0.244302837823993i | 0.000000001 | 0.000192558139534884+0.874213953488374i | 2.30607627906977+0.0001i | 0.000192559139534884+0.874213953488374i | 0.000356634668650645+2.01600408022726i | 2.3062688382093+0.874313953488374i | 0.289882588164289+0.764245546451745i | 0.289982588164289+0.519942708627752i | 45.4 | 0.59534
[34 empty] | 45.6 | 0.0001-0.243231334149326i | 0.000000001 | 0.000192558139534884+0.878065116279072i | 2.30607627906977+0.0001i | 0.000192559139534884+0.878065116279072i | 0.000356249552371575+2.02488515538572i | 2.3062688382093+0.878165116279072i | 0.292116671771489+0.766761643332741i | 0.292216671771489+0.523530309183415i | 45.6 | 0.59956
[34 empty] | 45.8 | 0.0001-0.242169188585355i | 0.000000001 | 0.000192558139534884+0.88191627906977i | 2.30607627906977+0.0001i | 0.000192559139534884+0.88191627906977i | 0.000355864436092505+2.03376623054419i | 2.3062688382093+0.88201627906977i | 0.294355596847324+0.769268427382074i | 0.294455596847324+0.527099238796719i | 45.8 | 0.60377
[34 empty] | 46 | 0.0001-0.241116279069767i | 0.000000001 | 0.000192558139534884+0.885767441860467i | 2.30607627906977+0.0001i | 0.000192559139534884+0.885767441860467i | 0.000355479319813435+2.04264730570265i | 2.3062688382093+0.885867441860467i | 0.296599314618191+0.771765893080473i | 0.296699314618191+0.530649614010706i | 46 | 0.60796
[34 empty] | 46.2 | 0.0001-0.24007248565388i | 0.000000001 | 0.000192558139534884+0.889618604651165i | 2.30607627906977+0.0001i | 0.000192559139534884+0.889618604651165i | 0.000355094203534365+2.05152838086111i | 2.3062688382093+0.889718604651165i | 0.298847776387804+0.774254035204632i | 0.298947776387804+0.534181549550752i | 46.2 | 0.61214
[34 empty] | 46.4 | 0.0001-0.239037690457096i | 0.000000001 | 0.000192558139534884+0.893469767441863i | 2.30607627906977+0.0001i | 0.000192559139534884+0.893469767441863i | 0.000354709087255296+2.06040945601958i | 2.3062688382093+0.893569767441863i | 0.301100933539115+0.776732848825812i | 0.301200933539115+0.537695158368716i | 46.4 | 0.61631
[34 empty] | 46.6 | 0.0001-0.238011777622517i | 0.000000001 | 0.000192558139534884+0.897320930232561i | 2.30607627906977+0.0001i | 0.000192559139534884+0.897320930232561i | 0.000354323970976226+2.06929053117804i | 2.3062688382093+0.897420930232561i | 0.303358737536227+0.779202329308417i | 0.303458737536227+0.5411905516859i | 46.6 | 0.62046
[34 empty] | 46.8 | 0.0001-0.236994633273702i | 0.000000001 | 0.000192558139534884+0.901172093023258i | 2.30607627906977+0.0001i | 0.000192559139534884+0.901172093023258i | 0.000353938854697156+2.07817160633651i | 2.3062688382093+0.901272093023258i | 0.305621139926292+0.78166247230861i | 0.305721139926292+0.544667839034908i | 46.8 | 0.6246
[34 empty] | 47 | 0.0001-0.235986145472538i | 0.000000001 | 0.000192558139534884+0.905023255813956i | 2.30607627906977+0.0001i | 0.000192559139534884+0.905023255813956i | 0.000353553738418086+2.08705268149497i | 2.3062688382093+0.905123255813956i | 0.307888092341382+0.784113273772845i | 0.307988092341382+0.548127128300307i | 47 | 0.62873
[34 empty] | 47.2 | 0.0001-0.234986204178163i | 0.000000001 | 0.000192558139534884+0.908874418604654i | 2.30607627906977+0.0001i | 0.000192559139534884+0.908874418604654i | 0.000353168622139017+2.09593375665343i | 2.3062688382093+0.908974418604654i | 0.310159546500346+0.786554729936463i | 0.310259546500346+0.5515685257583i | 47.2 | 0.63284
[34 empty] | 47.4 | 0.0001-0.233994701206947i | 0.000000001 | 0.000192558139534884+0.912725581395352i | 2.30607627906977+0.0001i | 0.000192559139534884+0.912725581395352i | 0.000352783505859947+2.1048148318119i | 2.3062688382093+0.912825581395352i | 0.312435454210651+0.788986837322218i | 0.312535454210651+0.554992136115271i | 47.4 | 0.63694
[34 empty] | 47.6 | 0.0001-0.233011530193472i | 0.000000001 | 0.000192558139534884+0.916576744186049i | 2.30607627906977+0.0001i | 0.000192559139534884+0.916576744186049i | 0.000352398389580877+2.11369590697036i | 2.3062688382093+0.916676744186049i | 0.314715767370193+0.791409592738813i | 0.314815767370193+0.558398062545341i | 47.6 | 0.64103
[34 empty] | 47.8 | 0.0001-0.232036586552495i | 0.000000001 | 0.000192558139534884+0.920427906976747i | 2.30607627906977+0.0001i | 0.000192559139534884+0.920427906976747i | 0.000352013273301807+2.12257698212883i | 2.3062688382093+0.920527906976747i | 0.317000437969105+0.793822993279446i | 0.317100437969105+0.561786406726951i | 47.8 | 0.6451
[34 empty] | 48 | 0.0001-0.23106976744186i | 0.000000001 | 0.000192558139534884+0.924279069767445i | 2.30607627906977+0.0001i | 0.000192559139534884+0.924279069767445i | 0.000351628157022737+2.13145805728729i | 2.3062688382093+0.924379069767445i | 0.319289418091528+0.796227036320301i | 0.319389418091528+0.565157268878441i | 48 | 0.64916
[34 empty] | 48.2 | 0.0001-0.230110971726333i | 0.000000001 | 0.000192558139534884+0.928130232558142i | 2.30607627906977+0.0001i | 0.000192559139534884+0.928130232558142i | 0.000351243040743668+2.14033913244575i | 2.3062688382093+0.928230232558142i | 0.321582659917383+0.798621719519076i | 0.321682659917383+0.568510747792743i | 48.2 | 0.65321
[34 empty] | 48.4 | 0.0001-0.22916009994234i | 0.000000001 | 0.000192558139534884+0.93198139534884i | 2.30607627906977+0.0001i | 0.000192559139534884+0.93198139534884i | 0.000350857924464598+2.14922020760422i | 2.3062688382093+0.93208139534884i | 0.323880115724107+0.80100704081347i | 0.323980115724107+0.57184694087113i | 48.4 | 0.65725
[34 empty] | 48.6 | 0.0001-0.228217054263565i | 0.000000001 | 0.000192558139534884+0.935832558139538i | 2.30607627906977+0.0001i | 0.000192559139534884+0.935832558139538i | 0.000350472808185528+2.15810128276268i | 2.3062688382093+0.935932558139538i | 0.326181737888374+0.80338299841966i | 0.326281737888374+0.575165944156095i | 48.6 | 0.66127
[34 empty] | 48.8 | 0.0001-0.227281738467403i | 0.000000001 | 0.000192558139534884+0.939683720930236i | 2.30607627906977+0.0001i | 0.000192559139534884+0.939683720930236i | 0.000350087691906458+2.16698235792115i | 2.3062688382093+0.939783720930236i | 0.32848747888781+0.805749590830801i | 0.32858747888781+0.578467852363398i | 48.8 | 0.66528
[34 empty] | 49 | 0.0001-0.22635405790223i | 0.000000001 | 0.000192558139534884+0.943534883720933i | 2.30607627906977+0.0001i | 0.000192559139534884+0.943534883720933i | 0.000349702575627389+2.17586343307961i | 2.3062688382093+0.943634883720933i | 0.330797291302666+0.808106816815465i | 0.330897291302666+0.581752758913235i | 49 | 0.66928
[34 empty] | 49.2 | 0.0001-0.225433919455473i | 0.000000001 | 0.000192558139534884+0.947386046511631i | 2.30607627906977+0.0001i | 0.000192559139534884+0.947386046511631i | 0.000349317459348319+2.18474450823808i | 2.3062688382093+0.947486046511631i | 0.333111127817495+0.810454675416129i | 0.333211127817495+0.585020755960656i | 49.2 | 0.67326
[34 empty] | 49.4 | 0.0001-0.224521231522455i | 0.000000001 | 0.000192558139534884+0.951237209302329i | 2.30607627906977+0.0001i | 0.000192559139534884+0.951237209302329i | 0.000348932343069249+2.19362558339654i | 2.3062688382093+0.951337209302329i | 0.335428941222789+0.812793165947594i | 0.335528941222789+0.588271934425139i | 49.4 | 0.67723
[34 empty] | 49.6 | 0.0001-0.223615903975993i | 0.000000001 | 0.000192558139534884+0.955088372093027i | 2.30607627906977+0.0001i | 0.000192559139534884+0.955088372093027i | 0.000348547226790179+2.20250665855501i | 2.3062688382093+0.955188372093027i | 0.337750684416621+0.815122287995459i | 0.337850684416621+0.591506384019466i | 49.6 | 0.68119
[34 empty] | 49.8 | 0.0001-0.222717848136732i | 0.000000001 | 0.000192558139534884+0.958939534883724i | 2.30607627906977+0.0001i | 0.000192559139534884+0.958939534883724i | 0.00034816211051111+2.21138773371347i | 2.3062688382093+0.959039534883724i | 0.340076310406235+0.817442041414519i | 0.340176310406235+0.594724193277787i | 49.8 | 0.68514
[34 empty] | 50 | 0.0001-0.221826976744185i | 0.000000001 | 0.000192558139534884+0.962790697674422i | 2.30607627906977+0.0001i | 0.000192559139534884+0.962790697674422i | 0.00034777699423204+2.22026880887193i | 2.3062688382093+0.962890697674422i | 0.342405772309657+0.819752426327221i | 0.342505772309657+0.597925449583036i | 50 | 0.68908
𝐻=𝑋_𝐿/2𝜋𝑓×1000
(kvar/phase)
〖𝑄_(𝑅𝐴𝑇𝐸𝐷 𝑃𝐸𝑅 𝑃𝐻𝐴𝑆𝐸) =(𝑉_(𝐶𝐴𝑃 𝑅𝐴𝑇𝐼𝑁𝐺) )^2/𝑋_𝐶 ×1000〗_(kvar/phase)
V_(CAP FUNDAMENTAL VOLTAGE)=I_(RATED FUNDAMENTAL)× X_C/1000
𝑉_(𝐶𝐴𝑃 𝐻𝐴𝑅𝑀𝑂𝑁𝐼𝐶 𝑉𝑂𝐿𝑇𝐴𝐺𝐸)=𝑋_𝐶/𝑛×𝐼_𝑛
𝐼_𝐶𝐴𝑃= 𝐼_(𝑅𝐴𝑇𝐸𝐷 𝐹𝑈𝑁𝐷𝐴𝑀𝐸𝑁𝑇𝐴𝐿)/𝑁
(ohms)
𝑅=𝑋_𝐿×𝐷𝐹×ℎ (ohms)
𝐼_(𝑅𝐸𝑆𝐼𝑆𝑇𝑂𝑅 (𝑛))=𝑋_𝐿/〖𝑅+𝑗𝑋〗_𝐿 ×𝐼_𝑛
𝐼_(𝑅𝐸𝐴𝐶𝑇𝑂𝑅 (𝑛))=𝑅/〖𝑅+𝑗𝑋〗_𝐿 ×𝐼_𝑛
(kW/Phase)
𝑅_𝑊=√(∑_(𝑛=1)^𝑛▒〖〖𝐼_𝑛^ 〗_^2×𝑅〗)/1000 (kW/Phase)
(ohms)
𝑋_𝑒𝑓𝑓= 〖〖𝑘𝑉〗_𝐿𝐿𝑆𝑌𝑆〗^2/(𝑄_𝑒𝑓𝑓 (𝑀𝑉𝐴𝑅))×1000(ohms)
𝐼_(𝐹𝐼𝐿𝑇𝐸𝑅 𝑅𝑀𝑆 𝐶𝑈𝑅𝑅𝐸𝑁𝑇)=√(∑_(𝑛=1)^𝑛▒〖𝐼_𝑛^ 〗_^2 )
𝐼_(𝑅𝐴𝑇𝐸𝐷 𝐹𝑈𝑁𝐷𝐴𝑀𝐸𝑁𝑇𝐴𝐿)= (𝑄_𝑒𝑓𝑓 (𝑘𝑣𝑎𝑟))/(1.73×〖〖𝑘𝑉〗_𝐿𝐿𝑆𝑌𝑆〗^ )
𝑋_𝐶=(ℎ^2/(ℎ^2−1)) 𝑋_𝑒𝑓𝑓
𝐷𝐹= 𝑅/(ℎ×𝑋_𝐿 )
𝑋_𝐿=𝑋_𝐶/ℎ^2
𝐼_𝐹𝑈𝑆𝐸≥ 𝐼_𝐶𝐴𝑃×1.8
/1000
𝑉_(𝐶𝐴𝑃 𝑅𝑀𝑆 𝑉𝑂𝐿𝑇𝐴𝐺𝐸)=√(∑_(𝑛=1)^𝑛▒〖𝑉_(𝐶𝐴𝑃 𝐻𝐴𝑅𝑀𝑂𝑁𝐼𝐶 𝑉𝑂𝐿𝑇𝐴𝐺𝐸 (𝑉𝑂𝐿𝑇𝑆))〗^2 ) /1000
𝑉_(𝐶𝐴𝑃 𝑃𝐸𝐴𝐾 𝑉𝑂𝐿𝑇𝐴𝐺𝐸)=1.414 ×∑_(𝑛=1)^𝑛▒〖𝑉_(𝐶𝐴𝑃 𝐻𝐴𝑅𝑀𝑂𝑁𝐼𝐶 𝑉𝑂𝐿𝑇𝐴𝐺𝐸)〗^
/N
𝐼_(𝐶𝐴𝑃 𝑅𝑀𝑆 𝐶𝑈𝑅𝑅𝐸𝑁𝑇)=√(∑_(𝑛=1)^𝑛▒〖𝐼_𝑛^ 〗_^2 ) /N
/1000
𝑄_( 𝐶𝐴𝑃𝐴𝐶𝐼𝑇𝑂𝑅)=∑_(𝑛=1)^𝑛▒〖〖𝑋_𝑐/𝑛 𝑥 𝐼〗_𝑛^ 〗_^2 /1000

## C-High-Pass Filter Design
Rev: 7-27-2020 | [10 empty] | Click here to learn how to use this spreadsheet tool. You will be redirected to our YouTube Channel: https://youtu.be/sV6w9_-4ZJw | [23 empty] | PLOT (ohms) |  |  | (res branch) | (aux branch) | product of res branch and aux branch | sum of res branch and aux branch | power over sum rule of aux and res branch | add main cap in |  |  | SD - Standard Duty Capacitors, with -40C to +55C Temperature Rating
[34 empty] | HARM # | Xc main | Xc aux | XL (inductance) | Resistance | XCAUX + XL | [6 empty] | HD- Heavy Duty Capacitors, with -40C to +55C Temperature Rating
Northeast Power Systems, Inc. | [10 empty] | Contact NEPSI for assistance or to obtain a quote on your metal-enclosed harmonic filter system. Email us at: sales@nepsi.com | [22 empty] | 1 | 0.0001-38.088i | 0.000001-2.43176091208656i | 0.0243176091208656+2.43176091208656i | 19.8528960862747+0.0001i | 0.0243186091208656 | 0.482794819839277+2.43186091208656E-06i | 19.8772146953956+0.0001i | 0.0242888567255415+1.49680907410939E-10i | 0.0243888567255415-38.0879999998503i | 1 | 38.088 | EXD - Extreme Duty Capacitors, with -50C to +55C Temperature Rating
66 Carey Road, Queensbury, NY |  |  |  |  | Phone: (518) 792-4776 Fax: (518) 792-5767 www.nepsi.com | [28 empty] | 1.2 | 0.0001-31.74i | 0.000001-2.0264674267388i | 0.0243176091208656+2.91811309450387i | 19.8528960862747+0.0001i | 0.0243186091208656+0.89164566776507i | 0.4827056552725+17.7017512197779i | 19.8772146953956+0.89174566776507i | 0.0641080476578539+0.88767885321968i | 0.0642080476578539-30.8523211467803i | 1.2 | 30.8524
[34 empty] | 1.4 | 0.0001-27.2057142857143i | 0.000001-1.73697208006183i | 0.0243176091208656+3.40446527692118i | 19.8528960862747+0.0001i | 0.0243186091208656+1.66749319685935i | 0.482628070519591+33.1045715936796i | 19.8772146953956+1.66759319685935i | 0.162856947387184+1.65179040219156i | 0.162956947387184-25.5539238835227i | 1.4 | 25.5544
FILTER BANK DESIGN CALCULATIONS - C-HIGH-PASS FILTER DESIGN | [10 empty] | REVERSE CALCULATION USING C AND L | [22 empty] | 1.6 | 0.0001-23.805i | 0.000001-1.5198505700541i | 0.0243176091208656+3.89081745933849i | 19.8528960862747+0.0001i | 0.0243186091208656+2.37096688928439i | 0.482557723150348+47.0705617088219i | 19.8772146953956+2.37106688928439i | 0.302449723868926+2.33198835416415i | 0.302549723868926-21.4730116458359i | 1.6 | 21.4751
[34 empty] | 1.8 | 0.0001-21.16i | 0.000001-1.35097828449253i | 0.0243176091208656+4.3771696417558i | 19.8528960862747+0.0001i | 0.0243186091208656+3.02619135726327i | 0.482492200703551+60.0786649847912i | 19.8772146953956+3.02629135726327i | 0.473470414465186+2.95040358824318i | 0.473570414465186-18.2095964117568i | 1.8 | 18.2158
kVLLsys (System Line-to-Line Voltage Rating) |  | 13.8 | kV |  |  | Job Name: | Enter Job Name |  |  |  | CAPACITANCE - Main (µf)/Phase | 93.91 | (µf) | [20 empty] | 2 | 0.0001-19.044i | 0.000001-1.21588045604328i | 0.0243176091208656+4.86352182417311i | 19.8528960862747+0.0001i | 0.0243186091208656+3.64764136812983i | 0.482430055702464+72.4162474733393i | 19.8772146953956+3.64774136812983i | 0.670270858087315+3.52017492433941i | 0.670370858087315-15.5238250756606i | 2 | 15.5383 | (Rw) (Resistor KW/Phase) | 200
Qeff (3-Phase Output Rating of Filter) |  | 5000 | kvar |  |  | Stage/Branch Name | Branch/Stage # |  |  |  | CAPACITANCE - Aux (µf)/Phase | 49.69 | (µf) | [20 empty] | 2.2 | 0.0001-17.3127272727273i | 0.000001-1.10534586913025i | 0.0243176091208656+5.34987400659043i | 19.8528960862747+0.0001i | 0.0243186091208656+4.24452813746018i | 0.482370367025531+84.266178480127i | 19.8772146953956+4.24462813746018i | 0.88900633846224+4.04949478058187i | 0.88910633846224-13.2632324921454i | 2.2 | 13.293
h (Tuning Point of Filter) |  | 4.082 | (harmonic #) | [7 empty] | INDUCTANCE (mH) | 107.89 | mH | [20 empty] | 2.4 | 0.0001-15.87i | 0.000001-1.0132337133694i | 0.0243176091208656+5.83622618900774i | 19.8528960862747+0.0001i | 0.0243186091208656+4.82299247563834i | 0.482312520591713+95.7503708755936i | 19.8772146953956+4.82309247563834i | 1.12676472831136+4.54368893110469i | 1.12686472831136-11.3263110688953i | 2.4 | 11.3822
f (System Frequency) |  | 60 | (HZ) | [7 empty] | XL (Ohms) | 40.6724 | Ohms | [20 empty] | 2.6 | 0.0001-14.6492307692308i | 0.000001-0.93529265849483i | 0.0243176091208656+6.32257837142505i | 19.8528960862747+0.0001i | 0.0243186091208656+5.38728571293022i | 0.482256091267984+106.953225877737i | 19.8772146953956+5.38738571293022i | 1.3811508713098+5.00635702391909i | 1.3812508713098-9.64287374531171i | 2.6 | 9.7413
hFrequency |  | 244.92 | Hz | [7 empty] | Xc-MAIN (Ohms) | 28.2468 | Ohms | [20 empty] | 2.8 | 0.0001-13.6028571428571i | 0.000001-0.868486040030913i | 0.0243176091208656+6.80893055384236i | 19.8528960862747+0.0001i | 0.0243186091208656+5.94044451381145i | 0.482200775387896+117.93503007084i | 19.8772146953956+5.94054451381145i | 1.65007770672145+5.44003129512212i | 1.65017770672145-8.16282584773498i | 2.8 | 8.328
Xeff (effective reactance of Filter Bank) |  | 38.088 | Ohms | [7 empty] | Xc-MAIN (Ohms) | 53.3842 | Ohms | [20 empty] | 3 | 0.0001-12.696i | 0.000001-0.810586970695519i | 0.0243176091208656+7.29528273625967i | 19.8528960862747+0.0001i | 0.0243186091208656+6.48469576556415i | 0.482146350262721+128.739993616712i | 19.8772146953956+6.48479576556415i | 1.9316578705563+5.84657300422125i | 1.9317578705563-6.84942699577875i | 3 | 7.1166
IRATED FUNDAMENTAL |  | 209.4329 | amps | [7 empty] | h (Tuning Point) | 1.4167 | [21 empty] | 3.2 | 0.0001-11.9025i | 0.000001-0.759925285027049i | 0.0243176091208656+7.78163491867699i | 19.8528960862747+0.0001i | 0.0243186091208656+7.02170963364994i | 0.482092648875912+139.401274136707i | 19.8772146953956+7.02180963364994i | 2.22414670546666+6.22741874404989i | 2.22424670546666-5.67508125595011i | 3.2 | 6.0954
IFILTER RMS CURRENT |  | 231.2274 | amps | [7 empty] | Qeff | 4.6496 | MVAR | [20 empty] | 3.4 | 0.0001-11.2023529411765i | 0.000001-0.715223797672517i | 0.0243176091208656+8.2679871010943i | 19.8528960862747+0.0001i | 0.0243186091208656+7.55276330342178i | 0.482039543508935+149.944227458922i | 19.8772146953956+7.55286330342178i | 2.52591253268115+6.58373707728254i | 2.52601253268115-4.61861586389396i | 3.4 | 5.2643
DF (Damping Factor) |  | 2 | [31 empty] | 3.6 | 0.0001-10.58i | 0.000001-0.675489142246266i | 0.0243176091208656+8.75433928351161i | 19.8528960862747+0.0001i | 0.0243186091208656+8.07885014126535i | 0.48198693482515+160.388574782988i | 19.8772146953956+8.07895014126535i | 2.83542165755354+6.91652963903416i | 2.83552165755354-3.66347036096584i | 3.6 | 4.6326
R (Resistor Ohm Rating/Phase) |  | 19.8529 | Ohms | [7 empty] | CAPACITANCE CALCULATOR | [22 empty] | 3.8 | 0.0001-10.0231578947368i | 0.000001-0.639937082128041i | 0.0243176091208656+9.24069146592892i | 19.8528960862747+0.0001i | 0.0243186091208656+8.60075438380088i | 0.481934744400897+170.749885477031i | 19.8772146953956+8.60085438380088i | 3.1512313227596+7.22669679538039i | 3.1513313227596-2.79646109935641i | 3.8 | 4.2132
(Rw) (Resistor KW/Phase) |  | 48.979 | kW/Phase | [30 empty] | 4 | 0.0001-9.522i | 0.000001-0.607940228021639i | 0.0243176091208656+9.72704364834623i | 19.8528960862747+0.0001i | 0.0243186091208656+9.11910342032459i | 0.481882909497244+181.040615035557i | 19.8772146953956+9.11920342032459i | 3.47198681091913+7.51508012179915i | 3.47208681091913-2.00691987820085i | 4 | 4.0104
Ifundamental resistor current (actual) |  | 0 | amps | (C-HP Filters nearly eliminate fundamental losses in damping resistor) | [6 empty] | CAPACITOR KVAR | 490 | kvar | [6 empty] | ETAP 19.5.0 - INPUT EDITOR | [13 empty] | 4.2 | 0.0001-9.06857142857143i | 0.000001-0.578990693353942i | 0.0243176091208656+10.2133958307635i | 19.8528960862747+0.0001i | 0.0243186091208656+9.63440513740956i | 0.481831379325536+191.270846477924i | 19.8772146953956+9.63450513740956i | 3.79642052513203+7.7824894380502i | 3.79652052513203-1.28608199052123i | 4.2 | 4.0084
(Rw) (Resistor KW/Phase - Specified) |  | 73.4685 | kW/Phase | (at least 1.5X is recommended, if not 2X actual) | [6 empty] | CAPACITOR FREQUENCY | 60 | Hertz | [20 empty] | 4.4 | 0.0001-8.65636363636364i | 0.000001-0.552672934565127i | 0.0243176091208656+10.6997480131809i | 19.8528960862747+0.0001i | 0.0243186091208656+10.1470750786158i | 0.481780112331415+201.448829547248i | 19.8772146953956+10.1471750786158i | 4.12335179760889+8.02971942458103i | 4.12345179760889-0.62664421178261i | 4.4 | 4.1708
Ifundamental resistor current (specified) |  | 60.8329 | amps | [7 empty] | CAPACITOR VOLTAGE (kV) | 9.96 | kV | [6 empty] | ETAP Input Data | [13 empty] | 4.6 | 0.0001-8.28i | 0.000001-0.528643676540556i | 0.0243176091208656+11.1861001955982i | 19.8528960862747+0.0001i | 0.0243186091208656+10.6574565190576i | 0.481729074187371+211.581379248702i | 19.8772146953956+10.6575565190576i | 4.45168671677069+8.25755916887095i | 4.45178671677069-0.0224408311290496i | 4.6 | 4.4518
XC-MAIN |  | 38.088 | Ohms | [5 empty] | Main Cap Capacitance (per phase): | 69.65 micro-farads/Phase | CAPACITANCE (µf) | 13.1 | (µf) | [8 empty] | Capacitor C1 |  |  | Inductor L1 | [8 empty] | 4.8 | 0.0001-7.935i | 0.000001-0.506616856684699i | 0.0243176091208656+11.6724523780155i | 19.8528960862747+0.0001i | 0.0243186091208656+11.1658355213308i | 0.481678236287144+221.674174753276i | 19.8772146953956+11.1659355213308i | 4.78041758834665+8.46679692179137i | 4.78051758834665+0.531796921791371i | 4.8 | 4.81
XC-AUX |  | 2.4318 | Ohms | [5 empty] | Aux Cap Capacitance (per phase): | 1090.84 micro-farads/phase | CAPACITANCE (µf) | 13.1 | (µf) | [7 empty] | KVAR | 411.2246 |  | XL1 | 2.4318 |  | ohms | [6 empty] | 5 | 0.0001-7.6176i | 0.000001-0.486352182417311i | 0.0243176091208656+12.1588045604328i | 19.8528960862747+0.0001i | 0.0243186091208656+11.6724523780155i | 0.481627574601475+231.731986564593i | 19.8772146953956+11.6725523780155i | 5.10862184517726+8.65822164395866i | 5.10872184517726+1.04062164395866i | 5 | 5.2136
XL (Inductive reactance of reactor at system frequency) |  | 2.4318 | ohms | [7 empty] | Xc (Ohms) | 202.4522 | Ohms | [7 empty] | Uf | 1090.84 |  | Q Factor | 100 | [8 empty] | 5.2 | 0.0001-7.32461538461538i | 0.000001-0.467646329247415i | 0.0243176091208656+12.6451567428501i | 19.8528960862747+0.0001i | 0.0243186091208656+12.1775104136027i | 0.481577068797917+241.758851262643i | 19.8772146953956+12.1776104136027i | 5.43546034316546+8.83262245115537i | 5.43556034316546+1.50800706653999i | 5.2 | 5.6409
H (Inductance of Reactor) |  | 6.4506 | mH | [7 empty] | RATED CURRENT | 49.1968 | AMPS | [7 empty] | Rated kV | 1 |  | Max I | 231.2274 |  | Amps | [6 empty] | 5.4 | 0.0001-7.05333333333333i | 0.000001-0.450326094830844i | 0.0243176091208656+13.1315089252674i | 19.8528960862747+0.0001i | 0.0243186091208656+12.6811828304366i | 0.481526701556233+251.75820741557i | 19.8772146953956+12.6812828304366i | 5.7601750556653+8.99078674353956i | 5.7602750556653+1.93745341020623i | 5.4 | 6.0774
XX/R RATIO (X/R OF IRON-CORE REACTOR AT FUNDAMENTAL FREQUENCY) |  | 100 | Typically Near 100 | [17 empty] | Max. KV | 1.1 | [11 empty] | 5.6 | 0.0001-6.80142857142857i | 0.000001-0.434243020015457i | 0.0243176091208656+13.6178611076847i | 19.8528960862747+0.0001i | 0.0243186091208656+13.1836180876692i | 0.48147645803051+261.733002367489i | 19.8772146953956+13.1837180876692i | 6.08208622268674+9.13349757522841i | 6.08218622268674+2.33206900379984i | 5.6 | 6.5139
[34 empty] | 5.8 | 0.0001-6.56689655172414i | 0.000001-0.419269122773544i | 0.0243176091208656+14.104213290102i | 19.8528960862747+0.0001i | 0.0243186091208656+13.6849441673285i | 0.481426325422544+271.685776932305i | 19.8772146953956+13.6850441673285i | 6.40058903526091+9.26153065753647i | 6.40068903526091+2.69463410581233i | 5.8 | 6.9448
MAIN CAPACITOR PARAMETERS | [33 empty] | 6 | 0.0001-6.348i | 0.000001-0.405293485347759i | 0.0243176091208656+14.5905654725194i | 19.8528960862747+0.0001i | 0.0243186091208656+14.1852719871716i | 0.48137629264056+281.618733148722i | 19.8772146953956+14.1853719871716i | 6.71514994599425+9.37565127061426i | 6.71524994599425+3.02765127061426i | 6 | 7.3662
VCAP MAIN RATING |  | 9.96 | kV | [18 empty] | Capacitor C2 | [11 empty] | 6.2 | 0.0001-6.14322580645161i | 0.000001-0.392219501949445i | 0.0243176091208656+15.0769176549367i | 19.8528960862747+0.0001i | 0.0243186091208656+14.6846981529873i | 0.481326350023978+291.533788921428i | 19.8772146953956+14.6847981529873i | 7.02530269880945+9.47661127136733i | 7.02540269880945+3.33338546491572i | 6.2 | 7.7761
QMAIN RATED PER PHASE |  | 2604.5369 | kvar | [17 empty] | KVAR | 2604.5369 | [11 empty] | 6.4 | 0.0001-5.95125i | 0.000001-0.379962642513524i | 0.0243176091208656+15.563269837354i | 19.8528960862747+0.0001i | 0.0243186091208656+15.1833071948405i | 0.481276489119793+301.432622417016i | 19.8772146953956+15.1834071948405i | 7.33064416720524+9.56514632152654i | 7.33074416720524+3.61389632152654i | 6.4 | 8.1731
NMAIN Number of MAIN Caps Per Phase |  | 5 | [5 empty] | Main Cap Capacitive Reactance (per can): | 190.44 | Ohms/Capacitor | [10 empty] | Uf | 69.65 | [11 empty] | 6.6 | 0.0001-5.77090909090909i | 0.000001-0.368448623043418i | 0.0243176091208656+16.0496220197713i | 19.8528960862747+0.0001i | 0.0243186091208656+15.6811733967279i | 0.481226702499604+311.316708387955i | 19.8772146953956+15.6812733967279i | 7.63083008324444+9.64197341255354i | 7.63093008324444+3.87106432164445i | 6.6 | 8.5566
MAIN Capacitor Can KVAR Rating (kvar) |  | 520.9074 | kvar |  |  |  |  | Main Cap Capacitance (per can): | 13.9291 | µF (micro-farads)/Capacitor | [10 empty] | Rated kV | 9.96 |  |  | Resistor | [8 empty] | 6.8 | 0.0001-5.60117647058823i | 0.000001-0.357611898836258i | 0.0243176091208656+16.5359742021886i | 19.8528960862747+0.0001i | 0.0243186091208656+16.1783623033523i | 0.481176983608942+321.187348086418i | 19.8772146953956+16.1784623033523i | 7.92557073038867+9.70778872942249i | 7.92567073038867+4.10661225883426i | 6.8 | 8.9264
ICAP MAIN (Fundamental Amps Each Main Capacitor) |  | 41.8866 | amps | [17 empty] | Max. KV | 10.956 |  | R | 19.8529 | [8 empty] | 7 | 0.0001-5.44114285714286i | 0.000001-0.347394416012365i | 0.0243176091208656+17.0223263846059i | 19.8528960862747+0.0001i | 0.0243186091208656+16.6749319685935i | 0.481127326642418+331.045694050048i | 19.8772146953956+16.6750319685935i | 8.21462666331637+9.76326587014935i | 8.21472666331637+4.32212301300649i | 7 | 9.2824
IMAN FUSE (Minimum Recommended Fuse Rating on Capacitors) |  | 75.3958 | amps | [30 empty] | 7.2 | 0.0001-5.29i | 0.000001-0.337744571123133i | 0.0243176091208656+17.5086785670232i | 19.8528960862747+0.0001i | 0.0243186091208656+17.1709339959001i | 0.481077726439687+340.892770756747i | 19.8772146953956+17.1710339959001i | 8.49780450770823+9.80905441996059i | 8.49790450770823+4.51905441996059i | 7.2 | 9.6248
VCAP MAIN FUNDAMENTAL VOLTAGE |  | 7.9769 | kV | [30 empty] | 7.4 | 0.0001-5.14702702702703i | 0.000001-0.328616339471156i | 0.0243176091208656+17.9950307494405i | 19.8528960862747+0.0001i | 0.0243186091208656+17.6664144099693i | 0.48102817839828+350.729491930047i | 19.8772146953956+17.6665144099693i | 8.77495288316899+9.84577886649654i | 8.77505288316899+4.69875183946951i | 7.4 | 9.9539
VCAP MAIN RMS VOLTAGE |  | 8.0117 | kV | [30 empty] | 7.6 | 0.0001-5.01157894736842i | 0.000001-0.319968541064021i | 0.0243176091208656+18.4813829318578i | 19.8528960862747+0.0001i | 0.0243186091208656+18.1614143907938i | 0.480978678400198+360.556675112064i | 19.8772146953956+18.1615143907938i | 9.0459584832908+9.87403783411963i | 9.0460584832908+4.86245888675121i | 7.6 | 10.2701
VCAP MAIN PEAK CAP VOLTAGE |  | 12.3349 | kV | [30 empty] | 7.8 | 0.0001-4.88307692307692i | 0.000001-0.311764219498276i | 0.0243176091208656+18.9677351142752i | 19.8528960862747+0.0001i | 0.0243186091208656+18.6559708947769i | 0.480929222749799+370.375053994432i | 19.8772146953956+18.6560708947769i | 9.31074233854658+9.89440361023338i | 9.31084233854658+5.01132668715646i | 7.8 | 10.5738
IMAIN CAP RMS CURRENT |  | 46.2455 | amps | [16 empty] | Power Factory - C-HP Filter Input | [13 empty] | 8 | 0.0001-4.761i | 0.000001-0.30397011401082i | 0.0243176091208656+19.4540872966925i | 19.8528960862747+0.0001i | 0.0243186091208656+19.1501171826817i | 0.480879808121009+380.185288899624i | 19.8772146953956+19.1502171826817i | 9.56925628033198+9.90742193372513i | 9.56935628033198+5.14642193372513i | 8 | 10.8655
QMAIN CAPACITROR (1-phase) |  | 1743.7799 | kvar | [30 empty] | 8.2 | 0.0001-4.64487804878049i | 0.000001-0.296556208791043i | 0.0243176091208656+19.9404394791098i | 19.8528960862747+0.0001i | 0.0243186091208656+19.6438832703188i | 0.480830431512245+389.98797572841i | 19.8772146953956+19.6439832703188i | 9.82147961807312+9.9136120146074i | 9.82157961807312+5.26873396582691i | 8.2 | 11.1455
[34 empty] | 8.4 | 0.0001-4.53428571428571i | 0.000001-0.289495346676971i | 0.0243176091208656+20.4267916615271i | 19.8528960862747+0.0001i | 0.0243186091208656+20.1372963148501i | 0.480781090207792+399.783653629102i | 19.8772146953956+20.1373963148501i | 10.0674160358742+9.91346675416607i | 10.0675160358742+5.37918103988036i | 8.4 | 11.4145
MAIN CAPACITOR DESIGN RATINGS VS IEEE/ANSI MAXIMUMS | [33 empty] | 8.6 | 0.0001-4.42883720930233i | 0.000001-0.282762896754251i | 0.0243176091208656+20.9131438439444i | 19.8528960862747+0.0001i | 0.0243186091208656+20.6303809471902i | 0.480731781744558+409.572811596689i | 19.8772146953956+20.6304809471902i | 10.3070907106383+9.90745313605344i | 10.3071907106383+5.47861592675111i | 8.6 | 11.6728
Capacitor Duty Rating: |  | HD- Heavy Duty Capacitors, with -40C to +55C Temperature Rating | [30 empty] | 9.96 | 8.8 | 0.0001-4.32818181818182i | 0.000001-0.276336467282563i | 0.0243176091208656+21.3994960263617i | 19.8528960862747+0.0001i | 0.0243186091208656+21.1231595590791i | 0.480682503883369+419.355894172058i | 19.8772146953956+21.1232595590791i | 10.5405476498833+9.89601276049495i | 10.5406476498833+5.56783094231313i | 8.8 | 11.9208
|  | Capacitor Design Values |  |  |  |  | Capacitor Design Values
|  | At Nominal Voltage | At 110% System Voltage | Capacitor Rating |  |  | At Nominal Voltage | At 110% System Voltage |  | Capacitor Rating | [22 empty] | 14.0834 | 9 | 0.0001-4.232i | 0.000001-0.270195656898506i | 0.0243176091208656+21.885848208779i | 19.8528960862747+0.0001i | 0.0243186091208656+21.6156525518805i | 0.480633254584089+429.133306381363i | 19.8772146953956+21.6157525518805i | 10.7678472445204+9.87956249588885i | 10.7679472445204+5.64756249588885i | 9 | 12.1591
% RATED VOLTS |  | 80.44% | 88.42% | 125% |  | % 60HZ AMPS: | 88.42% | 95.74% |  | 135% | [22 empty] | 52.2999 | 9.2 | 0.0001-4.14i | 0.000001-0.264321838270278i | 0.0243176091208656+22.3722003911963i | 19.8528960862747+0.0001i | 0.0243186091208656+22.107878552926i | 0.480584031983984+438.905418031082i | 19.8772146953956+22.107978552926i | 10.9890640295606+9.85849522439469i | 10.9891640295606+5.71849522439469i | 9.2 | 12.388
% CREST VOLTAGE |  | 87.58% | 97.58% | 135% |  | % 60HZ KVAR: | 66.95% | 80.42% |  | 135% | [22 empty] | 2604.5369 | 9.4 | 0.0001-4.05191489361702i | 0.000001-0.25869796937091i | 0.0243176091208656+22.8585525736136i | 19.8528960862747+0.0001i | 0.0243186091208656+22.5998546042427i | 0.480534834378853+448.672567454808i | 19.8772146953956+22.5999546042427i | 11.2042846439981+9.83318066050342i | 11.2043846439981+5.7812657668864i | 9.4 | 12.608
[34 empty] | 9.6 | 0.0001-3.9675i | 0.000001-0.25330842834235i | 0.0243176091208656+23.3449047560309i | 19.8528960862747+0.0001i | 0.0243186091208656+23.0915963276885i | 0.480485660206508+458.435064791663i | 19.8772146953956+23.0916963276885i | 11.4136059798898+9.80396622396496i | 11.4137059798898+5.83646622396496i | 9.6 | 12.8194
AUX CAPACITOR PARAMETERS | [33 empty] | 9.8 | 0.0001-3.8865306122449i | 0.000001-0.248138868580261i | 0.0243176091208656+23.8312569384483i | 19.8528960862747+0.0001i | 0.0243186091208656+23.583118069868i | 0.48043650803229+468.193194863298i | 19.8772146953956+23.583218069868i | 11.6171335098376+9.77117795075263i | 11.6172335098376+5.88464733850773i | 9.8 | 13.0226
VCAP AUX RATING |  | 1 | kV | [30 empty] | 10 | 0.0001-3.8088i | 0.000001-0.243176091208656i | 0.0243176091208656+24.3176091208656i | 19.8528960862747+0.0001i | 0.0243186091208656+24.0744330296569i | 0.480387376536311+477.947219705619i | 19.8772146953956+24.0745330296569i | 11.8149797816081+9.73512142792272i | 11.8150797816081+5.92632142792272i | 10 | 13.2181
QAUX RATED PER PHASE |  | 411.2246 | kvar | [30 empty] | 10.2 | 0.0001-3.73411764705883i | 0.000001-0.238407932557506i | 0.0243176091208656+24.8039613032829i | 19.8528960862747+0.0001i | 0.0243186091208656+24.5655533707254i | 0.480338264502204+487.697380802708i | 19.8772146953956+24.5656533707254i | 12.0072630684383+9.69608274025352i | 12.0073630684383+5.96196509319469i | 10.2 | 13.406
NAUX Number of Aux Caps Per Phase |  | 6 | [5 empty] | Aux Cap Capacitive Reactance (per can): | 14.5906 | Ohms/Capacitor | [23 empty] | 10.4 | 0.0001-3.66230769230769i | 0.000001-0.233823164623708i | 0.0243176091208656+25.2903134857002i | 19.8528960862747+0.0001i | 0.0243186091208656+25.0564903210765i | 0.480289170807169+497.44390106294i | 19.8772146953956+25.0565903210765i | 12.1941061636081+9.65432941840445i | 12.1942061636081+5.99202172609676i | 10.4 | 13.5869
AUX Capacitor Can Rating (kvar) |  | 68.5374 | kvar |  |  |  |  | Aux Cap Main Capacitance (per can): | 181.8066 | µF (micro-farads)/Capacitor | [23 empty] | 10.6 | 0.0001-3.59320754716981i | 0.000001-0.229411406800619i | 0.0243176091208656+25.7766656681175i | 19.8528960862747+0.0001i | 0.0243186091208656+25.5472542613169i | 0.480240094413145+507.186986571424i | 19.8772146953956+25.5473542613169i | 12.3756353080708+9.6101113800178i | 12.3757353080708+6.01690383284799i | 10.6 | 13.7609
ICAP AUX (Fundamental Amps Each Aux Capacitor) |  | 34.9055 | amps | [30 empty] | 10.8 | 0.0001-3.52666666666667i | 0.000001-0.225163047415422i | 0.0243176091208656+26.2630178505348i | 19.8528960862747+0.0001i | 0.0243186091208656+26.0378548031194i | 0.480191034358965+516.926828147699i | 19.8772146953956+26.0379548031194i | 12.5519792402796+9.56366185669063i | 12.5520792402796+6.03699519002396i | 10.8 | 13.9284
Minimum Recommended Fuse Rating (amps) on AUX Capacitors (if present) |  | 62.8299 | amps | [30 empty] | 11 | 0.0001-3.46254545454546i | 0.000001-0.221069173826051i | 0.0243176091208656+26.7493700329521i | 19.8528960862747+0.0001i | 0.0243186091208656+26.528300859126i | 0.480141989753364+526.663602733521i | 19.8772146953956+26.528400859126i | 12.7232683577892+9.5151983010812i | 12.7233683577892+6.05265284653574i | 11 | 14.0897
VCAP AUX FUNDAMENTAL VOLTAGE |  | 0.50929 | kV | [30 empty] | 11.2 | 0.0001-3.40071428571429i | 0.000001-0.217121510007729i | 0.0243176091208656+27.2357222153694i | 19.8528960862747+0.0001i | 0.0243186091208656+27.0186007053617i | 0.480092959768741+536.397474631955i | 19.8772146953956+27.0187007053617i | 12.8896339807267+9.46492326958768i | 12.8897339807267+6.06420898387339i | 11.2 | 14.245
VCAP AUX RMS VOLTAGE |  | 0.51095 | kV | [30 empty] | 11.4 | 0.0001-3.34105263157895i | 0.000001-0.213312360709347i | 0.0243176091208656+27.7220743977867i | 19.8528960862747+0.0001i | 0.0243186091208656+27.5087620370774i | 0.480043943635569+546.128596616017i | 19.8772146953956+27.5088620370774i | 13.0512077077845+9.41302527706121i | 13.0513077077845+6.07197264548226i | 11.4 | 14.3946
VCAP AUX PEAK CAP VOLTAGE |  | 0.77823 | kV | [30 empty] | 11.6 | 0.0001-3.28344827586207i | 0.000001-0.209634561386772i | 0.0243176091208656+28.208426580204i | 19.8528960862747+0.0001i | 0.0243186091208656+27.9987920188172i | 0.479994940637395+555.857110922656i | 19.8772146953956+27.9988920188172i | 13.2081208559743+9.35967962089977i | 13.2082208559743+6.0762313450377i | 11.6 | 14.5388
ICAP AUX RMS CURRENT |  | 37.6383 | AMPS | [30 empty] | 11.8 | 0.0001-3.2277966101695i | 0.000001-0.206081433227675i | 0.0243176091208656+28.6947787626214i | 19.8528960862747+0.0001i | 0.0243186091208656+28.4886973293937i | 0.479945950106338+565.583150145646i | 19.8772146953956+28.4887973293937i | 13.360503975975+9.30504917262778i | 13.360603975975+6.07725256245828i | 11.8 | 14.6778
QAUX CAPACITROR (1-phase) |  | 110.1332 | kvar | [30 empty] | 12 | 0.0001-3.174i | 0.000001-0.20264674267388i | 0.0243176091208656+29.1811309450387i | 19.8528960862747+0.0001i | 0.0243186091208656+28.9784842023648i | 0.47989697141904+575.306838039162i | 19.8772146953956+28.9785842023648i | 13.508486435502+9.24928513571135i | 13.508586435502+6.07528513571135i | 12 | 14.8119
[34 empty] | 12.2 | 0.0001-3.12196721311476i | 0.000001-0.199324664925128i | 0.0243176091208656+29.667483127456i | 19.8528960862747+0.0001i | 0.0243186091208656+29.4681584625309i | 0.479848003993024+585.028290242363i | 19.8772146953956+29.4682584625309i | 13.6521960637089+9.19252776890155i | 13.6522960637089+6.07056055578679i | 12.2 | 14.9411
Northeast Power Systems, Inc. | [33 empty] | 12.4 | 0.0001-3.07161290322581i | 0.000001-0.196109750974723i | 0.0243176091208656+30.1538353098733i | 19.8528960862747+0.0001i | 0.0243186091208656+29.9577255588986i | 0.479799047283387+594.74761493381i | 19.8772146953956+29.9578255588986i | 13.7917588501939+9.13490707485125i | 13.7918588501939+6.06329417162544i | 12.4 | 15.0658
C High-Pass Filter Design - Stage/Branch: Branch/Stage #, Tuning Point: 4.08, Reference: Enter Job Name | [9 empty] | Page 2 | [23 empty] | 12.6 | 0.0001-3.02285714285715i | 0.000001-0.192996897784648i | 0.0243176091208656+30.6401874922906i | 19.8528960862747+0.0001i | 0.0243186091208656+30.447190594506i | 0.479750100779826+604.464913423589i | 19.8772146953956+30.447290594506i | 13.9272986927243+9.07654345412494i | 13.9273986927243+6.05368631126779i | 12.6 | 15.1862
[34 empty] | 12.8 | 0.0001-2.975625i | 0.000001-0.189981321256763i | 0.0243176091208656+31.1265396747079i | 19.8528960862747+0.0001i | 0.0243186091208656+30.9365583534511i | 0.479701164003932+614.180280689899i | 19.8772146953956+30.9366583534511i | 14.0589371883064+9.01754832502536i | 14.0590371883064+6.04192332502536i | 12.8 | 15.3023
AUX CAPACITOR DESIGN RATINGS VS IEEE/ANSI MAXIMUMS | [33 empty] | 13 | 0.0001-2.92984615384616i | 0.000001-0.187058531698966i | 0.0243176091208656+31.6128918571252i | 19.8528960862747+0.0001i | 0.0243186091208656+31.4258333254262i | 0.479652236506734+623.893805866136i | 19.8772146953956+31.4259333254262i | 14.1867934627092+8.95802470990514i | 14.1868934627092+6.02817855605898i | 13 | 15.4145
Capacitor Duty Rating: |  | HD- Heavy Duty Capacitors, with -40C to +55C Temperature Rating | [31 empty] | 13.2 | 0.0001-2.88545454545455i | 0.000001-0.184224311521709i | 0.0243176091208656+32.0992440395425i | 19.8528960862747+0.0001i | 0.0243186091208656+31.9150197280208i | 0.479603317866475+633.605572683665i | 19.8772146953956+31.9151197280208i | 14.3109840340032+8.89806778882497i | 14.3110840340032+6.01261324337042i | 13.2 | 15.5228
|  | Capacitor Design Values |  |  |  |  | Capacitor Design Values
|  | At Nominal Voltage | At 110% System Voltage | Capacitor Rating |  |  | At Nominal Voltage | At 110% System Voltage |  | Capacitor Rating |  |  |  |  | 1 | [18 empty] | 13.4 | 0.0001-2.8423880597015i | 0.000001-0.181474694931833i | 0.0243176091208656+32.5855962219598i | 19.8528960862747+0.0001i | 0.0243186091208656+32.404121527028i | 0.479554407686574+643.315659874965i | 19.8772146953956+32.404221527028i | 14.431622706099+8.83776542156775i | 14.431722706099+5.99537736186625i | 13.4 | 15.6275
% RATED VOLTS |  | 51.09% | 56.17% | 125% |  | % FUND AMPS | 54.92% | 59.67% |  | 135% |  |  |  |  | 1.414 | [18 empty] | 13.6 | 0.0001-2.80058823529412i | 0.000001-0.178805949418129i | 0.0243176091208656+33.0719484043771i | 19.8528960862747+0.0001i | 0.0243186091208656+32.893142454959i | 0.479505505593781+653.024141541193i | 19.8772146953956+32.893242454959i | 14.5488204886574+8.77719863912941i | 14.5489204886574+5.97661040383529i | 13.6 | 15.7287
% CREST VOLTAGE |  | 55.04% | 65.04% | 135% |  | % FUND KVAR | 26.78% | 32.23% |  | 135% |  |  |  |  | 68.5374 | [18 empty] | 13.8 | 0.0001-2.76i | 0.000001-0.176214558846852i | 0.0243176091208656+33.5583005867945i | 19.8528960862747+0.0001i | 0.0243186091208656+33.3820860279477i | 0.479456611236482+662.731087487789i | 19.8772146953956+33.3821860279477i | 14.6626855401058+8.71644210588587i | 14.6627855401058+5.95644210588587i | 13.8 | 15.8264
[15 empty] | 411.2246 | [18 empty] | 14 | 0.0001-2.72057142857143i | 0.000001-0.173697208006183i | 0.0243176091208656+34.0446527692118i | 19.8528960862747+0.0001i | 0.0243186091208656+33.8709555612056i | 0.479407724283156+672.436563531304i | 19.8772146953956+33.8710555612056i | 14.7733231308243+8.65556455368792i | 14.7734231308243+5.93499312511649i | 14 | 15.921
[34 empty] | 14.2 | 0.0001-2.68225352112676i | 0.000001-0.1712507684568i | 0.0243176091208656+34.5310049516291i | 19.8528960862747+0.0001i | 0.0243186091208656+34.3597541831723i | 0.47935884442096+682.140631780323i | 19.8772146953956+34.3598541831723i | 14.8808356238712+8.59462918916534i | 14.8809356238712+5.91237566803858i | 14.2 | 16.0124
[34 empty] | 14.4 | 0.0001-2.645i | 0.000001-0.168872285561567i | 0.0243176091208656+35.0173571340464i | 19.8528960862747+0.0001i | 0.0243186091208656+34.8484848484848i | 0.479309971354428+691.843350892948i | 19.8772146953956+34.8485848484848i | 14.9853224708903+8.53369407553429i | 14.9854224708903+5.88869407553429i | 14.4 | 16.1009
[34 empty] | 14.6 | 0.0001-2.60876712328768i | 0.000001-0.166558966581271i | 0.0243176091208656+35.5037093164637i | 19.8528960862747+0.0001i | 0.0243186091208656+35.3371503498824i | 0.479261104804289+701.544776313142i | 19.8772146953956+35.3372503498824i | 15.0868802210991+8.47281249019694i | 15.0869802210991+5.86404536690926i | 14.6 | 16.1865
[15 empty] | 1 | 2 | 3 | 4 | 5 | 7 | 11 | 13 | [11 empty] | 14.8 | 0.0001-2.57351351351352i | 0.000001-0.164308169735578i | 0.0243176091208656+35.990061498881i | 19.8528960862747+0.0001i | 0.0243186091208656+35.8257533291454i | 0.479212244506362+711.244960487894i | 19.8772146953956+35.8258533291454i | 15.1856025414816+8.41203325940871i | 15.1857025414816+5.83851974589519i | 14.8 | 16.2694
Harmonic #: (n) |  | 1 | 2 | 3 | 4 | 5 | 7 | 11 | 13 |  |  |  |  | VCAP HARMONIC VOLTAGE (volts)^2 | 63630592.402 | 0 | 0 | 0 | 557299.277 | 0 | 0 | 0 | [11 empty] | 15 | 0.0001-2.5392i | 0.000001-0.162117394139104i | 0.0243176091208656+36.4764136812983i | 19.8528960862747+0.0001i | 0.0243186091208656+36.3142962871592i | 0.479163390210561+720.943953067024i | 19.8772146953956+36.3143962871592i | 15.2815802465212+8.35140107126184i | 15.2816802465212+5.81220107126184i | 15 | 16.3497
Filter Current (amps) (In) |  | 209.4329 | 0 | 0 | 0 | 98 | 0 | 0 | 0 |  |  |  |  | Filter Current (amps) (In)^2 | 43862.1211 | 0 | 0 | 0 | 9604 | 0 | 0 | 0 | [11 empty] | 15.2 | 0.0001-2.50578947368421i | 0.000001-0.159984270532011i | 0.0243176091208656+36.9627658637156i | 19.8528960862747+0.0001i | 0.0243186091208656+36.8027815931836i | 0.479114541679959+730.641801087198i | 19.8772146953956+36.8028815931836i | 15.374901335992+8.29095676820243i | 15.375001335992+5.78516729451822i | 15.2 | 16.4274
VCAP MAIN HARMONIC VOLTAGE (volts) |  | 7976.8786 | 0 | 0 | 0 | 746.5248 | 0 | 0 | 0 |  |  |  |  | kvar (single phase) MAIN CAP | 1670.6205 | 0 | 0 | 0 | 73.1594 | 0 | 0 | 0 | [11 empty] | 15.4 | 0.0001-2.47324675324676i | 0.000001-0.157906552732894i | 0.0243176091208656+37.4491180461329i | 19.8528960862747+0.0001i | 0.0243186091208656+37.2912114934i | 0.479065698689937+740.338549141624i | 19.8772146953956+37.2913114934i | 15.465651039501+8.23073762025942i | 15.465751039501+5.75749086701266i | 15.4 | 16.5027
IREACTOR CURRENT (amps) |  | 209.4329 | 0 | 0 | 0 | 84.4802 | 0 | 0 | 0 | [24 empty] | 15.6 | 0.0001-2.44153846153847i | 0.000001-0.155882109749139i | 0.0243176091208656+37.9354702285502i | 19.8528960862747+0.0001i | 0.0243186091208656+37.7795881188011i | 0.479016861027397+750.034239536677i | 19.8772146953956+37.7796881188011i | 15.5539118666216+8.1707775801212i | 15.5540118666216+5.72923911858273i | 15.6 | 16.5756
IRESISTOR CURRENT (amps) |  | 0 | 0 | 0 | 0 | 49.6699 | 0 | 0 | 0 | [24 empty] | 15.8 | 0.0001-2.41063291139241i | 0.000001-0.153908918486491i | 0.0243176091208656+38.4218224109676i | 19.8528960862747+0.0001i | 0.0243186091208656+38.2679134924811i | 0.478968028490029+759.728912436638i | 19.8772146953956+38.2680134924811i | 15.639763661599+8.11110752115071i | 15.639863661599+5.7004746097583i | 15.8 | 16.6463
Filter Voltage Distortion |  | 100.1% | 0% | 0% | 0% | 6.413% | 0% | 0% | 0% | [5 empty] | 17 | 19 | 23 | 25 | 29 | 31 | 35 | 37 | [11 empty] | 16 | 0.0001-2.3805i | 0.000001-0.15198505700541i | 0.0243176091208656+38.9081745933849i | 19.8528960862747+0.0001i | 0.0243186091208656+38.7561895363795i | 0.478919200885639+769.42260599757i | 19.8772146953956+38.7562895363795i | 15.7232836617296+8.05175545938165i | 15.7233836617296+5.67125545938165i | 16 | 16.7149
Harmonic #: (n) |  | 17 | 19 | 23 | 25 | 29 | 31 | 35 | 37 |  |  |  |  | VCAP HARMONIC VOLTAGE (volts)^2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [11 empty] | 16.2 | 0.0001-2.35111111111112i | 0.000001-0.150108698276948i | 0.0243176091208656+39.3945267758022i | 19.8528960862747+0.0001i | 0.0243186091208656+39.2444180775253i | 0.478870378031524+779.115356491291i | 19.8772146953956+39.2445180775253i | 15.8045465586261+7.9927467604906i | 15.8046465586261+5.64163564937948i | 16.2 | 16.7814
Filter Current (amps) (In) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | Filter Current (amps) (In)^2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [11 empty] | 16.4 | 0.0001-2.32243902439025i | 0.000001-0.148278104395522i | 0.0243176091208656+39.8808789582195i | 19.8528960862747+0.0001i | 0.0243186091208656+39.732600853824i | 0.478821559753895+788.807198420258i | 19.8772146953956+39.732700853824i | 15.8836245616804+7.93410433269063i | 15.8837245616804+5.61166530830038i | 16.4 | 16.8459
VCAP HARMONIC VOLTAGE (volts) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | kvar (single phase) MAIN CAP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [11 empty] | 16.6 | 0.0001-2.29445783132531i | 0.000001-0.146491621210034i | 0.0243176091208656+40.3672311406368i | 19.8528960862747+0.0001i | 0.0243186091208656+40.2207395194268i | 0.478772745887334+798.498164624163i | 19.8772146953956+40.2208395194268i | 15.9605874631222+7.87584880644345i | 15.9606874631222+5.58139097511814i | 16.6 | 16.9084
IREACTOR CURRENT (amps) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [24 empty] | 16.8 | 0.0001-2.26714285714286i | 0.000001-0.144747673338486i | 0.0243176091208656+40.8535833230541i | 19.8528960862747+0.0001i | 0.0243186091208656+40.7088356497156i | 0.478723936274305+808.1882863789i | 19.8772146953956+40.7089356497156i | 16.0355027041509+7.81799870183914i | 16.0356027041509+5.55085584469628i | 16.8 | 16.9692
IRESISTOR CURRENT (amps) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [24 empty] | 17 | 0.0001-2.2404705882353i | 0.000001-0.143044759534504i | 0.0243176091208656+41.3399355054714i | 19.8528960862747+0.0001i | 0.0243186091208656+41.1968907459369i | 0.478675130764683+817.877593488558i | 19.8772146953956+41.1969907459369i | 16.1084354416884+7.76057058444562i | 16.1085354416884+5.52009999621032i | 17 | 17.0281
Filter Voltage Distortion |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | [24 empty] | 17.2 | 0.0001-2.21441860465117i | 0.000001-0.141381448377126i | 0.0243176091208656+41.8262876878887i | 19.8528960862747+0.0001i | 0.0243186091208656+41.6849062395116i | 0.478626329215326+827.566114370989i | 19.8772146953956+41.6850062395116i | 16.1794486153613+7.70357921038433i | 16.1795486153613+5.48916060573316i | 17.2 | 17.0853
System Voltage Distortion (Vthd %) |  | 6.413% | [11 empty] | Table below handles the aux capacitor, inductor and resistor for loss, voltage, and rms calculations | [19 empty] | 17.4 | 0.0001-2.18896551724138i | 0.000001-0.139756374257848i | 0.0243176091208656+42.312639870306i | 19.8528960862747+0.0001i | 0.0243186091208656+42.1728834960482i | 0.478577531489672+837.253876137475i | 19.8772146953956+42.1729834960482i | 16.248603014377+7.64703766134432i | 16.248703014377+5.45807214410294i | 17.4 | 17.1409
FILTER ONE-LINE DIAGRAM | [13 empty] | harmonic # | 1 | 2 | 3 | 4 | 5 | 7 | 11 | 13 | 17 | 19 | 23 | 25 | 29 | 31 | 35 | 37 |  |  |  | 17.6 | 0.0001-2.16409090909091i | 0.000001-0.138168233641282i | 0.0243176091208656+42.7989920527233i | 19.8528960862747+0.0001i | 0.0243186091208656+42.660823819082i | 0.478528737457369+846.940904666968i | 19.8772146953956+42.660923819082i | 16.3159573440074+7.59095747020471i | 16.3160573440074+5.4268665611138i | 17.6 | 17.1949
Filter Bank Fundamental amps 209.4 amps/phase | [7 empty] | Reactor Fundamental Design Margin: | 1.5 |  |  |  |  | Total filter amps | 209.4329 | 0 | 0 | 0 | 98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 17.8 | 0.0001-2.13977528089888i | 0.000001-0.136615781577897i | 0.0243176091208656+43.2853442351406i | 19.8528960862747+0.0001i | 0.0243186091208656+43.1487284535627i | 0.478479946993921+856.627224675326i | 19.8772146953956+43.1488284535627i | 16.3815682914366+7.53534873789442i | 16.3816682914366+5.39557345699554i | 17.8 | 17.2474
Filter Bank RMS AMPS 231.23 amps/phase | [7 empty] | Reactor Harmonic Design Margin: | 1.5 |  |  |  |  | Total filter amps^2 | 43862.1211 | 0 | 0 | 0 | 9604 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 231.2274 | Filter Bank RMS Amps |  | 18 | 0.0001-2.116i | 0.000001-0.135097828449253i | 0.0243176091208656+43.771696417558i | 19.8528960862747+0.0001i | 0.0243186091208656+43.6365985891087i | 0.478431159980366+866.312859779917i | 19.8772146953956+43.6366985891087i | 16.4454905907655+7.48022024207953i | 16.4455905907655+5.36422024207953i | 18 | 17.2983
[14 empty] | R, XL, XCA EQUIVALENT IMPEDANCE (ohms) | 0 | 3.5876 | 6.1642 | 8.2867 | 10.0622 | 12.7686 | 15.8948 | 16.7842 | 17.8845 | 18.2324 | 18.7053 | 18.8692 | 19.1084 | 19.197 | 19.3331 | 19.3859 |  |  |  | 18.2 | 0.0001-2.09274725274726i | 0.000001-0.133613236927833i | 0.0243176091208656+44.2580485999753i | 19.8528960862747+0.0001i | 0.0243186091208656+44.1244353630475i | 0.478382376302972+875.997832559988i | 19.8772146953956+44.1245353630475i | 16.5077770870043+7.4255795382314i | 16.5078770870043+5.33283228548414i | 18.2 | 17.3479
Iron-Core Filter Reactor: 2.43 ohms, 6.45 mH | [5 empty] | Reference: C-High-Pass Filter Design - Stage/Branch: , Tuning Point: 4.08, Reference: Enter Job Name | [7 empty] | Voltage Across Resistor (volts) | 0 | 0 | 0 | 0 | 986.091 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 18.4 | 0.0001-2.07i | 0.000001-0.132160919135139i | 0.0243176091208656+44.7444007823926i | 19.8528960862747+0.0001i | 0.0243186091208656+44.6122398632575i | 0.478333595852951+885.682164613074i | 19.8772146953956+44.6123398632575i | 16.5684787989081+7.37143305359328i | 16.5685787989081+5.30143305359328i | 18.4 | 17.3961
I1= 209.4 amps nominal | [13 empty] | I REACTOR & AUX CAP (AMPS) | 209.4329 | 0 | 0 | 0 | 84.4802 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 18.6 | 0.0001-2.04774193548388i | 0.000001-0.130739833983149i | 0.0243176091208656+45.2307529648099i | 19.8528960862747+0.0001i | 0.0243186091208656+45.1000131308268i | 0.478284818526194+895.36587660779i | 19.8772146953956+45.1001131308268i | 16.6276449805417+7.31778617453031i | 16.6277449805417+5.27004423904643i | 18.6 | 17.4429
[6 empty] | Current Ratings |  |  | Design & Construction Details |  |  |  |  | I RESISTOR (amps) | 0 | 0 | 0 | 0 | 49.6699 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 49.6699 | RESISTOR RMS AMPS |  | 18.8 | 0.0001-2.02595744680851i | 0.000001-0.129348984685455i | 0.0243176091208656+45.7171051472272i | 19.8528960862747+0.0001i | 0.0243186091208656+45.5877561625417i | 0.478236044223023+905.04898833323i | 19.8772146953956+45.5878561625417i | 16.6853231814782+7.26464332771587i | 16.6854231814782+5.23868588090736i | 18.8 | 17.4885
High-Pass Resistor: 19.9 ohms/Phase | [5 empty] | Harm # | Amps |  | Quantity: | 3 |  |  |  | I RESISTOR^2 | 0 | 0 | 0 | 0 | 2467.0972 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 19 | 0.0001-2.00463157894737i | 0.000001-0.127987416425609i | 0.0243176091208656+46.2034573296445i | 19.8528960862747+0.0001i | 0.0243186091208656+46.0754699132189i | 0.478187272847955+914.731518745272i | 19.8772146953956+46.0755699132189i | 16.74155930556+7.21200805557767i | 16.74165930556+5.2073764766303i | 19 | 17.5328
49 KW/Phase Total | [5 empty] | 1 | 314.1493 |  | Number of Phases: | 3 |  |  |  | Resistor losses (kW) | 0 | 0 | 0 | 0 | 48.979 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 19.2 | 0.0001-1.98375i | 0.000001-0.126654214171175i | 0.0243176091208656+46.6898095120618i | 19.8528960862747+0.0001i | 0.0243186091208656+46.5631552978906i | 0.478138504309488+924.413486009954i | 19.8772146953956+46.5632552978906i | 16.7963976681651+7.15988308639911i | 16.7964976681651+5.17613308639911i | 19.2 | 17.576 |  |  | 314.1493 | 98689.7725
49.67 RMS Amps | [5 empty] | 2 | 0 |  | System Voltage: | 13.8 kV |  |  |  | Vcap aux Harmonic Voltage | 509.2906 | 0 | 0 | 0 | 41.0871 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 19.4 | 0.0001-1.96329896907217i | 0.000001-0.125348500623019i | 0.0243176091208656+47.1761616944791i | 19.8528960862747+0.0001i | 0.0243186091208656+47.0508131938561i | 0.478089738519891+934.094907544209i | 19.8772146953956+47.0509131938561i | 16.8498810519377+7.1082703994446i | 16.8499810519377+5.14497143037243i | 19.4 | 17.618 |  |  | 0 | 0
[6 empty] | 3 | 0 |  | BIL Rating (kV): | 95 |  |  |  | Vcap aux harmonic voltage^2 | 259376.9484 | 0 | 0 | 0 | 1688.1519 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 19.6 | 0.0001-1.94326530612245i | 0.000001-0.124069434290131i | 0.0243176091208656+47.6625138768964i | 19.8528960862747+0.0001i | 0.0243186091208656+47.5384444426063i | 0.478040975395016+943.775800054067i | 19.8772146953956+47.5385444426063i | 16.9020507609567+7.05717128545349i | 16.9021507609567+5.11390597933104i | 19.6 | 17.6588 |  |  | 0 | 0
Aux Capacitor: Qty(18), 69 kvar, 1 kV, 181.81 µF/Can | [5 empty] | 4 | 0 |  | Fundamental Frequency: | 60 |  |  |  | (I REACTOR & AUX CAP)^2 | 43862.1211 | 0 | 0 | 0 | 7136.9028 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 19.8 | 0.0001-1.92363636363637i | 0.000001-0.12281620768114i | 0.0243176091208656+48.1488660593137i | 19.8528960862747+0.0001i | 0.0243186091208656+48.0260498516326i | 0.477992214854114+953.456179570571i | 19.8772146953956+48.0261498516326i | 16.9529466733243+7.00658640282337i | 16.9530466733243+5.082950039187i | 19.8 | 17.6986 |  |  | 0 | 0
Optional Capacitor Fuse: 63 (Minimum Amps) | [5 empty] | 5 | 147 |  | Inductance (mH): | 6.4506 |  |  |  | KVAR (SINGLE PHASE) AUX CAP | 106.6622 | 0 | 0 | 0 | 3.471 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 20 | 0.0001-1.9044i | 0.000001-0.121588045604328i | 0.0243176091208656+48.6352182417311i | 19.8528960862747+0.0001i | 0.0243186091208656+48.5136301961268i | 0.477943456819664+963.136061483525i | 19.8772146953956+48.5137301961268i | 17.0026072921698+6.95651582978221i | 17.0027072921698+5.05211582978221i | 20 | 17.7374 |  |  | 147 | 21609
[6 empty] | 7 | 0 |  | Reactance at 60Hz (ohms): | 2.4318 |  |  |  | I2R REACTOR LOSSES | 1066.6219 | 0 | 0 | 0 | 173.5524 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 20.2 | 0.0001-1.88554455445545i | 0.000001-0.120384203568642i | 0.0243176091208656+49.1215704241484i | 19.8528960862747+0.0001i | 0.0243186091208656+49.0011862205798i | 0.477894701217219+972.815460573227i | 19.8772146953956+49.0012862205798i | 17.0510697950683+6.90695911282807i | 17.0511697950683+5.02141455837262i | 20.2 | 17.7752 |  |  | 0 | 0
Main Capacitor Fuse: 75 (Minimum Amps) | [5 empty] | 11 | 0 |  | Taps: | None | [23 empty] | 20.4 | 0.0001-1.86705882352942i | 0.000001-0.119203966278753i | 0.0243176091208656+49.6079226065657i | 19.8528960862747+0.0001i | 0.0243186091208656+49.4887186402869i | 0.477845947975248+982.494391040363i | 19.8772146953956+49.4888186402869i | 17.0983700818854+6.85791531169639i | 17.0984700818854+4.99085648816697i | 20.4 | 17.812 |  |  | 0 | 0
[6 empty] | 13 | 0 |  | Insulation Type: | Nomex | [23 empty] | 20.6 | 0.0001-1.84893203883496i | 0.000001-0.118046646217794i | 0.0243176091208656+50.094274788983i | 19.8528960862747+0.0001i | 0.0243186091208656+49.9762281427652i | 0.477797197025+992.172866534136i | 19.8772146953956+49.9763281427652i | 17.1445428210618+6.80938304109659i | 17.1446428210618+4.96045100226163i | 20.6 | 17.8478 |  |  | 0 | 0
[6 empty] | 17 | 0 |  | Ambient: | 60C | [23 empty] | 20.8 | 0.0001-1.83115384615385i | 0.000001-0.116911582311854i | 0.0243176091208656+50.5806269714003i | 19.8528960862747+0.0001i | 0.0243186091208656+50.4637153890884i | 0.477748448300368+1001.85090017877i | 19.8772146953956+50.4638153890884i | 17.189621494358+6.76136050944372i | 17.189721494358+4.93020666328987i | 20.8 | 17.8828 |  |  | 0 | 0
[6 empty] | 19 | 0 |  | Temperature Rise: | 115C Rise over Ambient | [23 empty] | 21 | 0.0001-1.81371428571429i | 0.000001-0.115798138670789i | 0.0243176091208656+51.0669791538176i | 19.8528960862747+0.0001i | 0.0243186091208656+50.9511810151468i | 0.477699701737762+1011.52850459854i | 19.8772146953956+50.9512810151468i | 17.2336384400841+6.71384555479464i | 17.2337384400841+4.90013126908035i | 21 | 17.9168 |  |  | 0 | 0
Main Capacitor: Qty(15), 521 kvar, 9.96 kV, 13.93 µF/Can | [5 empty] | 23 | 0 |  | Winding Type: | CU/AL - Based On Price | [23 empty] | 21.2 | 0.0001-1.79660377358491i | 0.000001-0.11470570340031i | 0.0243176091208656+51.5533313362349i | 19.8528960862747+0.0001i | 0.0243186091208656+51.4386256328346i | 0.477650957275993+1021.20569194131i | 19.8772146953956+51.4387256328346i | 17.276624894841+6.6668356781839i | 17.276724894841+4.87023190459899i | 21.2 | 17.9501 |  |  | 0 | 0
[6 empty] | 25 | 0 |  | Tack Winding to Core: | Yes | [23 empty] | 21.4 | 0.0001-1.77981308411215i | 0.000001-0.11363368748068i | 0.0243176091208656+52.0396835186522i | 19.8528960862747+0.0001i | 0.0243186091208656+51.9260498311715i | 0.47760221485616+1030.88247390083i | 19.8772146953956+51.9261498311715i | 17.3186110338064+6.62032807454165i | 17.3187110338064+4.8405149904295i | 21.4 | 17.9824 |  |  | 0 | 0
[6 empty] | 29 | 0 |  | Enclosure: | None/Open Construction | [23 empty] | 21.6 | 0.0001-1.76333333333334i | 0.000001-0.112581523707711i | 0.0243176091208656+52.5260357010695i | 19.8528960862747+0.0001i | 0.0243186091208656+52.4134541773618i | 0.477553474421541+1040.55886173775i | 19.8772146953956+52.4135541773618i | 17.359626009596+6.57431966136198i | 17.359726009596+4.81098632802864i | 21.6 | 18.014 |  |  | 0 | 0
13.8kV, 60Hz C-High-Pass Filter, Wye-Connected | [5 empty] | 31 | 0 | [26 empty] | 21.8 | 0.0001-1.74715596330276i | 0.000001-0.111548665692044i | 0.0243176091208656+53.0123878834868i | 19.8528960862747+0.0001i | 0.0243186091208656+52.9008392177948i | 0.477504735917497+1050.23486629947i | 19.8772146953956+52.9009392177948i | 17.3996979897358+6.52880710527964i | 17.3997979897358+4.78165114197688i | 21.8 | 18.0449 |  |  | 0 | 0
5.00 MVAR 3-Phase, 4.1 Tuning | [5 empty] | 35 | 0 | [26 empty] | 22 | 0.0001-1.73127272727273i | 0.000001-0.110534586913026i | 0.0243176091208656+53.4987400659042i | 19.8528960862747+0.0001i | 0.0243186091208656+53.3882054789912i | 0.477455999291378+1059.91049803895i | 19.8772146953956+53.3883054789912i | 17.438854192783+6.48378684670134i | 17.438954192783+4.75251411942861i | 22 | 18.0749 |  |  | 0 | 0
[6 empty] | 37 | 0 | [26 empty] | 22.2 | 0.0001-1.71567567567568i | 0.000001-0.109538779823719i | 0.0243176091208656+53.9850922483215i | 19.8528960862747+0.0001i | 0.0243186091208656+53.8755534684978i | 0.477407264492427+1069.58576703248i | 19.8772146953956+53.8756534684978i | 17.4771209231299+6.43925512262792i | 17.4772209231299+4.72357944695224i | 22.2 | 18.1043 |  |  | 0 | 0
[6 empty] | RMS: | 346.8411 | [26 empty] | 22.4 | 0.0001-1.70035714285715i | 0.000001-0.108560755003864i | 0.0243176091208656+54.4714444307388i | 19.8528960862747+0.0001i | 0.0243186091208656+54.3628836757349i | 0.477358531471703+1079.26068299646i | 19.8772146953956+54.3629836757349i | 17.5145236045307+6.39520798779371i | 17.5146236045307+4.69485084493656i | 22.4 | 18.1329 |  |  |  | 120298.7725
[34 empty] | 22.6 | 0.0001-1.68530973451328i | 0.000001-0.107600040357813i | 0.0243176091208656+54.9577966131561i | 19.8528960862747+0.0001i | 0.0243186091208656+54.8501965727983i | 0.477309800181997+1088.93525530337i | 19.8772146953956+54.8502965727983i | 17.5510868123895+6.35164133424188i | 17.5511868123895+4.6663315997286i | 22.6 | 18.1609 |  |  |  | 346.8411 | reactor RMS amps (for supplier with margin)
Where: | [33 empty] | 22.8 | 0.0001-1.67052631578948i | 0.000001-0.106656180354674i | 0.0243176091208656+55.4441487955734i | 19.8528960862747+0.0001i | 0.0243186091208656+55.3374926152187i | 0.477261070577755+1098.60949299679i | 19.8772146953956+55.3375926152187i | 17.5868343048462+6.30855090944434i | 17.5869343048462+4.63802459365486i | 22.8 | 18.1882
Xeff | Effective reactance of the harmonic filter | [32 empty] | 23 | 0.0001-1.656i | 0.000001-0.105728735308111i | 0.0243176091208656+55.9305009779907i | 19.8528960862747+0.0001i | 0.0243186091208656+55.8247722426826i | 0.477212342615009+1108.28340480579i | 19.8772146953956+55.8248722426826i | 17.6217890527012+6.26593233306949i | 17.6218890527012+4.60993233306949i | 23 | 18.2149
Qeff | Effective Reactive Power (MVAR) of the harmonic filter (fundamental current only, not including harmonics) | [32 empty] | 23.2 | 0.0001-1.64172413793104i | 0.000001-0.104817280693386i | 0.0243176091208656+56.416853160408i | 19.8528960862747+0.0001i | 0.0243186091208656+56.3120358797146i | 0.477163616251305+1117.95699915841i | 19.8772146953956+56.3121358797146i | 17.655973268214+6.22378111249116i | 17.656073268214+4.58205697456012i | 23.2 | 18.2409
QFILTER | Kvar rating of harmonic filter. Includes reactive power associated with fundamental and harmonic current. | [32 empty] | 23.4 | 0.0001-1.62769230769231i | 0.000001-0.103921406499426i | 0.0243176091208656+56.9032053428253i | 19.8528960862747+0.0001i | 0.0243186091208656+56.7992839363259i | 0.477114891445644+1127.63028419455i | 19.8772146953956+56.7993839363259i | 17.6894084328157+6.18209265712834i | 17.6895084328157+4.55440034943603i | 23.4 | 18.2664
QMAIN RATED PER PHASE | kvar rating of MAAIN capacitors at their rated voltage (not the application voltage) | [32 empty] | 23.6 | 0.0001-1.61389830508475i | 0.000001-0.103040716613837i | 0.0243176091208656+57.3895575252426i | 19.8528960862747+0.0001i | 0.0243186091208656+57.2865168086288i | 0.477066168158414+1137.3032677782i | 19.8772146953956+57.2866168086288i | 17.7221153237723+6.14086229169735i | 17.7222153237723+4.5269639866126i | 23.6 | 18.2913
VLLSYS | Nominal System Line-to-Line Voltage | [32 empty] | 23.8 | 0.0001-1.60033613445379i | 0.000001-0.102174828238931i | 0.0243176091208656+57.8759097076599i | 19.8528960862747+0.0001i | 0.0243186091208656+57.773734879421i | 0.477017446351335+1146.97595750899i | 19.8772146953956+57.773834879421i | 17.7541140398334+6.10008526845234i | 17.7542140398334+4.49974913399855i | 23.8 | 18.3156
XC | Capacitive reactance of the harmonic filter capacitor at fundamental frequency | [32 empty] | 24 | 0.0001-1.587i | 0.000001-0.10132337133694i | 0.0243176091208656+58.3622618900772i | 19.8528960862747+0.0001i | 0.0243186091208656+58.2609385187403i | 0.476968725987403+1156.64836073325i | 19.8772146953956+58.2610385187403i | 17.7854240259054+6.05975677848617i | 17.7855240259054+4.47275677848617i | 24 | 18.3393
XL | Inductive Reactance of the harmonic filter reactor at fundamental frequency | [32 empty] | 24.2 | 0.0001-1.57388429752067i | 0.000001-0.100485988102751i | 0.0243176091208656+58.8486140724946i | 19.8528960862747+0.0001i | 0.0243186091208656+58.7481280843918i | 0.476920007030838+1166.32048455445i | 19.8772146953956+58.7482280843918i | 17.8160640967816+6.01987196215684i | 17.8161640967816+4.44598766463617i | 24.2 | 18.3625
h | harmonic number of tuning filter tuning point | [32 empty] | 24.4 | 0.0001-1.56098360655738i | 0.000001-0.0996623324625641i | 0.0243176091208656+59.3349662549119i | 19.8528960862747+0.0001i | 0.0243186091208656+59.2353039224493i | 0.476871289447032+1175.99233584315i | 19.8772146953956+59.2354039224493i | 17.8460524599645+5.98042591870135i | 17.8461524599645+4.41944231214397i | 24.4 | 18.3852
f | frequency | [32 empty] | 24.6 | 0.0001-1.54829268292683i | 0.000001-0.0988520695970148i | 0.0243176091208656+59.8213184373292i | 19.8528960862747+0.0001i | 0.0243186091208656+59.7224663677322i | 0.476822573202504+1185.66392124648i | 19.8772146953956+59.7225663677322i | 17.8754067376144+5.94141371509439i | 17.8755067376144+4.39312103216756i | 24.6 | 18.4074
H | Reactor Henry Rating (milliHenrys) | [32 empty] | 24.8 | 0.0001-1.53580645161291i | 0.000001-0.0980548754873614i | 0.0243176091208656+60.3076706197465i | 19.8528960862747+0.0001i | 0.0243186091208656+60.2096157442591i | 0.476773858264851+1195.33524719717i | 19.8772146953956+60.2097157442591i | 17.904143987656+5.90283039420489i | 17.904243987656+4.36702394259198i | 24.8 | 18.4291
IRATED FUNDAMENTAL | Fundamental Current Rating of Filter Bank | [32 empty] | 25 | 0.0001-1.52352i | 0.000001-0.0972704364834625i | 0.0243176091208656+60.7940228021638i | 19.8528960862747+0.0001i | 0.0243186091208656+60.6967523656803i | 0.476725144602709+1205.00631992206i | 19.8772146953956+60.6968523656803i | 17.9322807240737+5.86467098229939i | 17.9323807240737+4.34115098229939i | 25 | 18.4504
VCAP FUNDAMENTAL VOLTAGE | Fundamental Voltage Drop Across Capacitor | [32 empty] | 25.2 | 0.0001-1.51142857142858i | 0.000001-0.0964984488923239i | 0.0243176091208656+61.2803749845811i | 19.8528960862747+0.0001i | 0.0243186091208656+61.1838765356888i | 0.476676432185708+1214.67714545035i | 19.8772146953956+61.1839765356888i | 17.9598329364297+5.82693049593972i | 17.9599329364297+4.31550192451114i | 25.2 | 18.4711
VCAP HARMONIC VOLTAGE | Harmonic Voltage Drop Across Capacitor | [32 empty] | 25.4 | 0.0001-1.49952755905512i | 0.000001-0.0957386185860852i | 0.0243176091208656+61.7667271669984i | 19.8528960862747+0.0001i | 0.0243186091208656+61.6709885484123i | 0.476627720984436+1224.34772962133i | 19.8772146953956+61.6710885484123i | 17.9868161086301+5.78960394831637i | 17.9869161086301+4.29007638926125i | 25.4 | 18.4915
VCAP MAIN RMS VOLTAGE | MAIN Capacitor RMS Voltage (Fundamental Voltage + Harmonic Voltages) | [32 empty] | 25.6 | 0.0001-1.4878125i | 0.000001-0.0949906606283814i | 0.0243176091208656+62.2530793494157i | 19.8528960862747+0.0001i | 0.0243186091208656+62.1580886887873i | 0.476579010970398+1234.0180780918i | 19.8772146953956+62.1581886887873i | 18.0132452369709+5.75268635505809i | 18.0133452369709+4.26487385505809i | 25.6 | 18.5113
VPEAK CAP VOLTAGE | Capacitor Voltage assuming or harmonics are coincident | [32 empty] | 25.8 | 0.0001-1.47627906976745i | 0.000001-0.0942542989180838i | 0.0243176091208656+62.739431531833i | 19.8528960862747+0.0001i | 0.0243186091208656+62.6451772329149i | 0.476530302115985+1243.68819634318i | 19.8772146953956+62.6452772329149i | 18.039134847492+5.71617273955533i | 18.039234847492+4.23989366978788i | 25.8 | 18.5308
N | Number of Capacitors per phase | [32 empty] | 26 | 0.0001-1.46492307692308i | 0.000001-0.0935292658494832i | 0.0243176091208656+63.2257837142503i | 19.8528960862747+0.0001i | 0.0243186091208656+63.1322544484008i | 0.476481594394437+1253.35808968822i | 19.8772146953956+63.1323544484008i | 18.064499012663+5.68005813783099i | 18.064599012663+4.21513506090791i | 26 | 18.5499
VCAP var rating | Capacitor Can Var Rating (in Kvar) | [32 empty] | 26.2 | 0.0001-1.45374045801527i | 0.000001-0.0928153019880368i | 0.0243176091208656+63.7121358966677i | 19.8528960862747+0.0001i | 0.0243186091208656+63.6193205946797i | 0.476432887779809+1263.02776327743i | 19.8772146953956+63.6194205946797i | 18.08935136743+5.64433760299138i | 18.08945136743+4.19059714497611i | 26.2 | 18.5685
ICAP RMS CURRENT | RMS Current Seen By Capacitor (amps) | [32 empty] | 26.4 | 0.0001-1.44272727272728i | 0.000001-0.0921121557608547i | 0.0243176091208656+64.198488079085i | 19.8528960862747+0.0001i | 0.0243186091208656+64.1063759233241i | 0.476384182246945+1272.69722210528i | 19.8772146953956+64.1064759233241i | 18.1137051246484+5.60900620928768i | 18.1138051246484+4.1662789365604i | 26.4 | 18.5868
IFILTER RMS CURRENT | RMS Current into Filter Branch (amps) | [32 empty] | 26.6 | 0.0001-1.43187969924812i | 0.000001-0.091419583161149i | 0.0243176091208656+64.6848402615023i | 19.8528960862747+0.0001i | 0.0243186091208656+64.5934206783411i | 0.476335477771443+1282.36647101599i | 19.8772146953956+64.5935206783411i | 18.1375730899214+5.57405905581414i | 18.1376730899214+4.14217935656602i | 26.6 | 18.6046
DF | Damping Factor is defined as the resistance of the resistor to the reactance of the reactor at the filter tuned frequency | [32 empty] | 26.8 | 0.0001-1.42119402985075i | 0.000001-0.0907373474659165i | 0.0243176091208656+65.1711924439196i | 19.8528960862747+0.0001i | 0.0243186091208656+65.0804550964537i | 0.476286774329632+1292.03551470922i | 19.8772146953956+65.0805550964537i | 18.1609676758753+5.53949126987131i | 18.1610676758753+4.11829724002056i | 26.8 | 18.6222
* Formulas taken From IEEE Std. 1531-2003 - IEEE Guide for Application and Specification of Harmonic Filters | [33 empty] | 27 | 0.0001-1.41066666666667i | 0.000001-0.090065218966169i | 0.0243176091208656+65.6575446263369i | 19.8528960862747+0.0001i | 0.0243186091208656+65.5674794073707i | 0.47623807189854+1301.70435774535i | 19.8772146953956+65.5675794073707i | 18.1839009158861+5.50529801001611i | 18.1840009158861+4.09463134334944i | 27 | 18.6393
[34 empty] | 27.2 | 0.0001-1.40029411764706i | 0.000001-0.0894029747090648i | 0.0243176091208656+66.1438968087542i | 19.8528960862747+0.0001i | 0.0243186091208656+66.0544938340451i | 0.476189370455872+1311.37300455063i | 19.8772146953956+66.0545938340451i | 18.2063844772841+5.4714744688228i | 18.2064844772841+4.07118035117574i | 27.2 | 18.6561
[34 empty] | 27.4 | 0.0001-1.39007299270073i | 0.000001-0.0887503982513344i | 0.0243176091208656+66.6302489911715i | 19.8528960862747+0.0001i | 0.0243186091208656+66.5414985929202i | 0.476140669979985+1321.0414594221i | 19.8772146953956+66.5415985929202i | 18.2284296740558+5.43801587537525i | 18.2285296740558+4.04794288267452i | 27.4 | 18.6726
Northeast Power Systems, Inc. | [33 empty] | 27.6 | 0.0001-1.38i | 0.000001-0.0881072794234262i | 0.0243176091208656+67.1166011735888i | 19.8528960862747+0.0001i | 0.0243186091208656+67.0284938941654i | 0.47609197044986+1330.70972653222i | 19.8772146953956+67.0285938941654i | 18.2500474790626+5.4049174975096i | 18.2501474790626+4.0249174975096i | 27.6 | 18.6887
C High-Pass Filter Design - Stage/Branch: Branch/Stage #, Tuning Point: 4.08, Reference: Enter Job Name | [9 empty] | Page 3 | [23 empty] | 27.8 | 0.0001-1.37007194244605i | 0.000001-0.0874734141038332i | 0.0243176091208656+67.6029533560061i | 19.8528960862747+0.0001i | 0.0243186091208656+67.5154799419023i | 0.476043271845087+1340.37780993341i | 19.8772146953956+67.5155799419023i | 18.2712485357962+5.37217464382621i | 18.2713485357962+4.00210270138016i | 27.8 | 18.7045
[34 empty] | 28 | 0.0001-1.36028571428572i | 0.000001-0.0868486040030916i | 0.0243176091208656+68.0893055384234i | 19.8528960862747+0.0001i | 0.0243186091208656+68.0024569344203i | 0.475994574145835+1350.04571356228i | 19.8772146953956+68.0025569344203i | 18.2920431696889+5.33978266548693i | 18.2921431696889+3.97949695120121i | 28 | 18.72
[34 empty] | 28.2 | 0.0001-1.35063829787234i | 0.000001-0.0862326564569703i | 0.0243176091208656+68.5756577208408i | 19.8528960862747+0.0001i | 0.0243186091208656+68.4894250643838i | 0.475945877332839+1359.71344124377i | 19.8772146953956+68.4895250643838i | 18.3124413989962+5.30773695781412i | 18.3125413989962+3.95709865994178i | 28.2 | 18.7352
[34 empty] | 28.4 | 0.0001-1.34112676056338i | 0.000001-0.0856253842284001i | 0.0243176091208656+69.0620099032581i | 19.8528960862747+0.0001i | 0.0243186091208656+68.9763845190297i | 0.475897181387374+1369.38099669508i | 19.8772146953956+68.9764845190297i | 18.3324529452702+5.27603296170574i | 18.3325529452702+3.93490620114236i | 28.4 | 18.7501
[34 empty] | 28.6 | 0.0001-1.33174825174826i | 0.000001-0.085026605317712i | 0.0243176091208656+69.5483620856754i | 19.8528960862747+0.0001i | 0.0243186091208656+69.4633354803577i | 0.475848486291241+1379.04838352944i | 19.8772146953956+69.4634354803577i | 18.3520872434379+5.24466616487997i | 18.3521872434379+3.91291791313171i | 28.6 | 18.7647
[34 empty] | 28.8 | 0.0001-1.3225i | 0.000001-0.0844361427807835i | 0.0243176091208656+70.0347142680927i | 19.8528960862747+0.0001i | 0.0243186091208656+69.9502781253119i | 0.475799792026746+1388.71560525969i | 19.8772146953956+69.9503781253119i | 18.3713534515018+5.2136321029622i | 18.3714534515018+3.8911321029622i | 28.8 | 18.779
[34 empty] | 29 | 0.0001-1.31337931034483i | 0.000001-0.0838538245547091i | 0.0243176091208656+70.52106645051i | 19.8528960862747+0.0001i | 0.0243186091208656+70.4372126259553i | 0.475751098576681+1398.38266530179i | 19.8772146953956+70.4373126259553i | 18.390260459878+5.18292636042644i | 18.390360459878+3.86954705008161i | 29 | 18.7931
[34 empty] | 29.2 | 0.0001-1.30438356164384i | 0.000001-0.0832794832906357i | 0.0243176091208656+71.0074186329273i | 19.8528960862747+0.0001i | 0.0243186091208656+70.9241391496367i | 0.475702405924313+1408.04956697809i | 19.8772146953956+70.9242391496367i | 18.4088169003845+5.15254457140155i | 18.4089169003845+3.84816100975771i | 29.2 | 18.8068
[34 empty] | 29.4 | 0.0001-1.29551020408164i | 0.000001-0.0827129561934205i | 0.0243176091208656+71.4937708153446i | 19.8528960862747+0.0001i | 0.0243186091208656+71.4110578591512i | 0.475653714053362+1417.71631352054i | 19.8772146953956+71.4111578591512i | 18.4270311548962+5.1224824203531i | 18.4271311548962+3.82697221627146i | 29.4 | 18.8203
[34 empty] | 29.6 | 0.0001-1.28675675675676i | 0.000001-0.0821540848677893i | 0.0243176091208656+71.9801229977619i | 19.8528960862747+0.0001i | 0.0243186091208656+71.8979689128941i | 0.475605022947988+1427.38290807376i | 19.8772146953956+71.8980689128941i | 18.4449113636775+5.09273564265014i | 18.4450113636775+3.80597888589338i | 29.6 | 18.8336
[34 empty] | 29.8 | 0.0001-1.27812080536913i | 0.000001-0.0816027151706901i | 0.0243176091208656+72.4664751801792i | 19.8528960862747+0.0001i | 0.0243186091208656+72.3848724650085i | 0.475556332592776+1437.04935369792i | 19.8772146953956+72.3849724650085i | 18.4624654334063+5.06330002502546i | 18.4625654334063+3.78517921965633i | 29.8 | 18.8466
[34 empty] | 30 | 0.0001-1.2696i | 0.000001-0.0810586970695521i | 0.0243176091208656+72.9528273625966i | 19.8528960862747+0.0001i | 0.0243186091208656+72.871768665527i | 0.475507642972724+1446.71565337162i | 19.8772146953956+72.871868665527i | 18.4797010449028+5.03417140593831i | 18.4798010449028+3.76457140593831i | 30 | 18.8593
[34 empty] | 30.2 | 0.0001-1.26119205298014i | 0.000001-0.0805218845061776i | 0.0243176091208656+73.4391795450139i | 19.8528960862747+0.0001i | 0.0243186091208656+73.3586576605077i | 0.475458954073226+1456.38180999452i | 19.8772146953956+73.3587576605077i | 18.4966256605723+5.00534567584639i | 18.4967256605723+3.74415362286625i | 30.2 | 18.8719
[34 empty] | 30.4 | 0.0001-1.25289473684211i | 0.000001-0.0799921352660054i | 0.0243176091208656+73.9255317274312i | 19.8528960862747+0.0001i | 0.0243186091208656+73.8455395921652i | 0.47541026588006+1466.04782639i | 19.8772146953956+73.8456395921652i | 18.5132465315757+4.97681877739509i | 18.5133465315757+3.72392404055298i | 30.4 | 18.8842
[34 empty] | 30.6 | 0.0001-1.24470588235294i | 0.000001-0.0794693108525021i | 0.0243176091208656+74.4118839098485i | 19.8528960862747+0.0001i | 0.0243186091208656+74.332414598996i | 0.475361578379377+1475.71370530762i | 19.8772146953956+74.332514598996i | 18.5295707047374+4.9485867055299i | 18.5296707047374+3.70388082317696i | 30.6 | 18.8962
[34 empty] | 30.8 | 0.0001-1.23662337662338i | 0.000001-0.0789532763664469i | 0.0243176091208656+74.8982360922658i | 19.8528960862747+0.0001i | 0.0243186091208656+74.8192828158994i | 0.475312891557687+1485.37944942551i | 19.8772146953956+74.8193828158994i | 18.5456050292006+4.92064550753867i | 18.5457050292006+3.68402213091529i | 30.8 | 18.9081
[34 empty] | 31 | 0.0001-1.22864516129033i | 0.000001-0.0784439003898891i | 0.0243176091208656+75.3845882746831i | 19.8528960862747+0.0001i | 0.0243186091208656+75.3061443742932i | 0.475264205401848+1495.0450613527i | 19.8772146953956+75.3062443742932i | 18.5613561628414+4.89299128302943i | 18.5614561628414+3.6643461217391i | 31 | 18.9197
[34 empty] | 31.2 | 0.0001-1.22076923076923i | 0.000001-0.0779410548745693i | 0.0243176091208656+75.8709404571004i | 19.8528960862747+0.0001i | 0.0243186091208656+75.7929994022258i | 0.475215519899054+1504.71054363133i | 19.8772146953956+75.7930994022258i | 18.5768305784493+4.8656201838488i | 18.5769305784493+3.64485095307957i | 31.2 | 18.9311
[34 empty] | 31.4 | 0.0001-1.21299363057325i | 0.000001-0.0774446150346039i | 0.0243176091208656+76.3572926395177i | 19.8528960862747+0.0001i | 0.0243186091208656+76.2798480244831i | 0.475166835036829+1514.37589873875i | 19.8772146953956+76.2799480244831i | 18.592034569685+4.83852841394631i | 18.592134569685+3.62553478337306i | 31.4 | 18.9423
[34 empty] | 31.6 | 0.0001-1.20531645569621i | 0.000001-0.0769544592432457i | 0.0243176091208656+76.843644821935i | 19.8528960862747+0.0001i | 0.0243186091208656+76.7666903626918i | 0.475118150803008+1524.04112908961i | 19.8772146953956+76.7667903626918i | 18.6069742568233+4.81171222918926i | 18.6070742568233+3.60639577349305i | 31.6 | 18.9533
[34 empty] | 31.8 | 0.0001-1.19773584905661i | 0.000001-0.0764704689335397i | 0.0243176091208656+77.3299970043523i | 19.8528960862747+0.0001i | 0.0243186091208656+77.2535265354188i | 0.475069467185735+1533.7062370378i | 19.8772146953956+77.2536265354188i | 18.6216555922892+4.78516793713206i | 18.6217555922892+3.58743208807545i | 31.8 | 18.9642
[34 empty] | 32 | 0.0001-1.19025i | 0.000001-0.0759925285027051i | 0.0243176091208656+77.8163491867696i | 19.8528960862747+0.0001i | 0.0243186091208656+77.7403566582669i | 0.47502078417345+1543.37122487837i | 19.8772146953956+77.7404566582669i | 18.636084365997+4.75889189674465i | 18.636184365997+3.56864189674465i | 32 | 18.9748
[34 empty] | 32.2 | 0.0001-1.18285714285715i | 0.000001-0.0755205252200796i | 0.0243176091208656+78.3027013691869i | 19.8528960862747+0.0001i | 0.0243186091208656+78.2271808439668i | 0.47497210175488+1553.03609484935i | 19.8772146953956+78.2272808439668i | 18.6502662104978+4.73288051810313i | 18.6503662104978+3.55002337524598i | 32.2 | 18.9852
[34 empty] | 32.4 | 0.0001-1.17555555555556i | 0.000001-0.0750543491384742i | 0.0243176091208656+78.7890535516043i | 19.8528960862747+0.0001i | 0.0243186091208656+78.7139992024658i | 0.47492341991903+1562.70084913352i | 19.8772146953956+78.7140992024658i | 18.6642066059444+4.70713026204653i | 18.6643066059444+3.53157470649097i | 32.4 | 18.9955
[34 empty] | 32.6 | 0.0001-1.16834355828221i | 0.000001-0.0745938930087903i | 0.0243176091208656+79.2754057340216i | 19.8528960862747+0.0001i | 0.0243186091208656+79.2008118410128i | 0.474874738655176+1572.36548986008i | 19.8772146953956+79.2009118410128i | 18.6779108848801+4.68163763980259i | 18.6780108848801+3.51329408152038i | 32.6 | 19.0056
[34 empty] | 32.8 | 0.0001-1.16121951219512i | 0.000001-0.0741390521977611i | 0.0243176091208656+79.7617579164389i | 19.8528960862747+0.0001i | 0.0243186091208656+79.6876188642411i | 0.474826057952853+1582.0300191063i | 19.8772146953956+79.6877188642411i | 18.6913842368582+4.65639921258579i | 18.6914842368582+3.49517970039067i | 32.8 | 19.0155
[34 empty] | 33 | 0.0001-1.15418181818182i | 0.000001-0.0736897246086837i | 0.0243176091208656+80.2481100988562i | 19.8528960862747+0.0001i | 0.0243186091208656+80.1744203742475i | 0.474777377801852+1591.6944388991i | 19.8772146953956+80.1745203742475i | 18.7046317128996+4.63141159117029i | 18.7047317128996+3.47722977298847i | 33 | 19.0252
[34 empty] | 33.2 | 0.0001-1.14722891566265i | 0.000001-0.0732458106050169i | 0.0243176091208656+80.7344622812736i | 19.8528960862747+0.0001i | 0.0243186091208656+80.6612164706686i | 0.47472869819221+1601.35875121655i | 19.8772146953956+80.6613164706686i | 18.7176582297931+4.60667143544036i | 18.7177582297931+3.45944251977771i | 33.2 | 19.0348
Filter Losses | [33 empty] | 33.4 | 0.0001-1.14035928143713i | 0.000001-0.0728072129367234i | 0.0243176091208656+81.2208144636909i | 19.8528960862747+0.0001i | 0.0243186091208656+81.1480072507542i | 0.474680019114201+1611.02295798935i | 19.8772146953956+81.1481072507542i | 18.730468574246+4.58217545392075i | 18.730568574246+3.44181617248362i | 33.4 | 19.0442
Aux Capacitor Losses |  | 61.6837 | Watts, 3-Phase or 210 BTUs/Hour | [30 empty] | 33.6 | 0.0001-1.13357142857143i | 0.000001-0.0723738366692429i | 0.0243176091208656+81.7071666461082i | 19.8528960862747+0.0001i | 0.0243186091208656+81.634792809439i | 0.474631340558333+1620.68706110222i | 19.8772146953956+81.634892809439i | 18.7430674068896+4.55792040328906i | 18.7431674068896+3.42434897471763i | 33.6 | 19.0534
Main Capacitor Losses |  | 390.6805 | Watts, 3-Phase or 1333 BTUs/Hour | [30 empty] | 33.8 | 0.0001-1.12686390532545i | 0.000001-0.071945589114987i | 0.0243176091208656+82.1935188285255i | 19.8528960862747+0.0001i | 0.0243186091208656+82.1215732394105i | 0.474582662515336+1630.35106239527i | 19.8772146953956+82.1216732394105i | 18.755459266146+4.53390308787244i | 18.755559266146+3.40703918254699i | 33.8 | 19.0625
Main Capacitor Fuse Losses |  | 2200.6874 | Watts, 3-Phase or 7509 BTUs/Hour | [30 empty] | 34 | 0.0001-1.12023529411765i | 0.000001-0.0715223797672518i | 0.0243176091208656+82.6798710109428i | 19.8528960862747+0.0001i | 0.0243186091208656+82.6083486311756i | 0.474533984976159+1640.01496366534i | 19.8772146953956+82.6084486311756i | 18.7676485719614+4.51012035913031i | 18.7677485719614+3.38988506501266i | 34 | 19.0714
Aux Capacitor Fuse Losses |  | 2233.6874 | Watts, 3-Phase or 7622 BTUs/Hour | [30 empty] | 34.2 | 0.0001-1.11368421052632i | 0.000001-0.0711041202364492i | 0.0243176091208656+83.1662231933601i | 19.8528960862747+0.0001i | 0.0243186091208656+83.0951190731236i | 0.474485307931965+1649.67876666721i | 19.8772146953956+83.0952190731236i | 18.7796396294101+4.48656911512487i | 18.7797396294101+3.37288490459855i | 34.2 | 19.0802
High Pass Resistor Losses, 60 Hertz |  | 0 | Watts, 3-Phase or 0 BTUs/Hour | [30 empty] | 34.4 | 0.0001-1.10720930232558i | 0.000001-0.0706907241885628i | 0.0243176091208656+83.6525753757775i | 19.8528960862747+0.0001i | 0.0243186091208656+83.5818846515889i | 0.474436631374118+1659.34247311485i | 19.8772146953956+83.5819846515889i | 18.7914366321743+4.46324629998104i | 18.7915366321743+3.35603699765546i | 34.4 | 19.0889
High Pass Resistor Losses, (harmonic) |  | 146937.0741 | Watts, 3-Phase or 501370 BTUs/Hour | [30 empty] | 34.6 | 0.0001-1.10080924855492i | 0.000001-0.0702821072857387i | 0.0243176091208656+84.1389275581948i | 19.8528960862747+0.0001i | 0.0243186091208656+84.0686454509091i | 0.474387955294186+1669.00608468263i | 19.8772146953956+84.0687454509091i | 18.8030436659069+4.44014890333777i | 18.8031436659069+3.33933965478285i | 34.6 | 19.0974
Iron-Core Reactor Losses, 60 Hertz |  | 3199.8657 | Watts, 3-Phase or 10918 BTUs/Hour | [30 empty] | 34.8 | 0.0001-1.09448275862069i | 0.000001-0.0698781871289242i | 0.0243176091208656+84.6252797406121i | 19.8528960862747+0.0001i | 0.0243186091208656+84.5554015534832i | 0.474339279683929+1678.66960300639i | 19.8772146953956+84.5555015534832i | 18.8144647114769+4.41727395979121i | 18.8145647114769+3.32279120117052i | 34.8 | 19.1057
Iron-Core Reactor Losses, (harmonic) |  | 520.6572 | Watts, 3-Phase or 1777 BTUs/Hour | [30 empty] | 35 | 0.0001-1.08822857142857i | 0.000001-0.0694788832024732i | 0.0243176091208656+85.1116319230294i | 19.8528960862747+0.0001i | 0.0243186091208656+85.0421530398269i | 0.474290604535294+1688.33302968461i | 19.8772146953956+85.0422530398269i | 18.8257036481063+4.39461854833199i | 18.8258036481063+3.30638997690342i | 35 | 19.114
[34 empty] | 35.2 | 0.0001-1.08204545454546i | 0.000001-0.0690841168206409i | 0.0243176091208656+85.5979841054467i | 19.8528960862747+0.0001i | 0.0243186091208656+85.5288999886261i | 0.474241929840414+1697.99636627944i | 19.8772146953956+85.5289999886261i | 18.8367642564003+4.37217979177719i | 18.8368642564003+3.29013433723173i | 35.2 | 19.122
Total 60 Hz Losses |  | 8086.6047 | Watts, 3-Phase or 27593 BTUs/Hour | [30 empty] | 35.4 | 0.0001-1.07593220338983i | 0.000001-0.0686938110758915i | 0.0243176091208656+86.084336287864i | 19.8528960862747+0.0001i | 0.0243186091208656+86.0156424767881i | 0.474193255591598+1707.65961431769i | 19.8772146953956+86.0157424767881i | 18.8476502212749+4.34995485619833i | 18.8477502212749+3.2740226528085i | 35.4 | 19.13
Total Harmonic Losses |  | 147457.7313 | Watts, 3-Phase or 503147 BTUs/Hour | [30 empty] | 35.6 | 0.0001-1.06988764044944i | 0.000001-0.0683078907889483i | 0.0243176091208656+86.5706884702814i | 19.8528960862747+0.0001i | 0.0243186091208656+86.5023805794925i | 0.474144581781328+1717.32277529191i | 19.8772146953956+86.5024805794925i | 18.8583651347868+4.32794095034652i | 18.8584651347868+3.25805330989708i | 35.6 | 19.1378
Total Harmonic Filter Losses |  | 155544.336 | Watts, 3-Phase or 530739 BTUs/Hour | [30 empty] | 35.8 | 0.0001-1.06391061452514i | 0.000001-0.0679262824605184i | 0.0243176091208656+87.0570406526987i | 19.8528960862747+0.0001i | 0.0243186091208656+86.9891143702382i | 0.474095908402253+1726.98585066126i | 19.8772146953956+86.9892143702382i | 18.8689124988682+4.30613532507534i | 18.8690124988682+3.2422247105502i | 35.8 | 19.1455
[34 empty] | 36 | 0.0001-1.058i | 0.000001-0.0675489142246267i | 0.0243176091208656+87.543392835116i | 19.8528960862747+0.0001i | 0.0243186091208656+87.4758439208914i | 0.474047235447188+1736.6488418525i | 19.8772146953956+87.4759439208914i | 18.8792957279697+4.2845352727627i | 18.8793957279697+3.2265352727627i | 36 | 19.1531
[34 empty] | 36.2 | 0.0001-1.0521546961326i | 0.000001-0.0671757158034961i | 0.0243176091208656+88.0297450175333i | 19.8528960862747+0.0001i | 0.0243186091208656+87.9625693017298i | 0.473998562909104+1746.31175026084i | 19.8772146953956+87.9626693017298i | 18.8895181516164+4.26313812673223i | 18.8896181516164+3.21098343059963i | 36.2 | 19.1606
[34 empty] | 36.4 | 0.0001-1.04637362637363i | 0.000001-0.0668066184639165i | 0.0243176091208656+88.5160971999506i | 19.8528960862747+0.0001i | 0.0243186091208656+88.4492905814867i | 0.473949890781128+1755.97457725083i | 19.8772146953956+88.4493905814867i | 18.8995830168787+4.24194126067502i | 18.8996830168787+3.19556763430139i | 36.4 | 19.1679
[34 empty] | 36.6 | 0.0001-1.04065573770492i | 0.000001-0.0664415549750426i | 0.0243176091208656+89.002449382368i | 19.8528960862747+0.0001i | 0.0243186091208656+88.936007827393i | 0.473901219056538+1765.63732415721i | 19.8772146953956+88.936107827393i | 18.9094934907616+4.22094208807251i | 18.9095934907616+3.18028635036759i | 36.6 | 19.1752
[34 empty] | 36.8 | 0.0001-1.035i | 0.000001-0.0660804595675695i | 0.0243176091208656+89.4888015647853i | 19.8528960862747+0.0001i | 0.0243186091208656+89.4227211052177i | 0.473852547728755+1775.29999228567i | 19.8772146953956+89.4228211052177i | 18.9192526625154+4.20013806162072i | 18.9193526625154+3.16513806162072i | 36.8 | 19.1823
[34 empty] | 37 | 0.0001-1.02940540540541i | 0.000001-0.0657232678942313i | 0.0243176091208656+89.9751537472026i | 19.8528960862747+0.0001i | 0.0243186091208656+89.9094304793084i | 0.473803876791346+1784.96258291371i | 19.8772146953956+89.9095304793084i | 18.9288635458712+4.179526672657i | 18.9289635458712+3.15012126725159i | 37 | 19.1893
[34 empty] | 37.2 | 0.0001-1.02387096774194i | 0.000001-0.0653699169915741i | 0.0243176091208656+90.4615059296199i | 19.8528960862747+0.0001i | 0.0243186091208656+90.3961360126283i | 0.473755206238014+1794.62509729132i | 19.8772146953956+90.3962360126283i | 18.9383290812021+4.15910545058921i | 18.9384290812021+3.13523448284727i | 37.2 | 19.1962
[34 empty] | 37.4 | 0.0001-1.01839572192513i | 0.000001-0.0650203452429561i | 0.0243176091208656+90.9478581120372i | 19.8528960862747+0.0001i | 0.0243186091208656+90.8828377667942i | 0.473706536062597+1804.28753664179i | 19.8772146953956+90.8829377667942i | 18.9476521376162+4.13887196232823i | 18.9477521376162+3.1204762404031i | 37.4 | 19.203
[34 empty] | 37.6 | 0.0001-1.01297872340426i | 0.000001-0.0646744923427276i | 0.0243176091208656+91.4342102944545i | 19.8528960862747+0.0001i | 0.0243186091208656+91.3695358021118i | 0.473657866259066+1813.94990216234i | 19.8772146953956+91.3696358021118i | 18.9568355149793+4.11882381172396i | 18.9569355149793+3.1058450883197i | 37.6 | 19.2097
[34 empty] | 37.8 | 0.0001-1.00761904761905i | 0.000001-0.0643322992615492i | 0.0243176091208656+91.9205624768719i | 19.8528960862747+0.0001i | 0.0243186091208656+91.8562301776103i | 0.473609196821516+1823.61219502489i | 19.8772146953956+91.8563301776103i | 18.9658819458746+4.09895863900547i | 18.9659819458746+3.09133959138642i | 37.8 | 19.2163
[34 empty] | 38 | 0.0001-1.00231578947368i | 0.000001-0.0639937082128041i | 0.0243176091208656+92.4069146592892i | 19.8528960862747+0.0001i | 0.0243186091208656+92.3429209510764i | 0.473560527744169+1833.27441637666i | 19.8772146953956+92.3430209510764i | 18.9747940974975+4.07927412022519i | 18.9748940974975+3.07695833075151i | 38 | 19.2228
[34 empty] | 38.2 | 0.0001-0.997068062827225i | 0.000001-0.0636586626200669i | 0.0243176091208656+92.8932668417065i | 19.8528960862747+0.0001i | 0.0243186091208656+92.8296081790864i | 0.473511859021368+1842.93656734086i | 19.8772146953956+92.8297081790864i | 18.9835745734912+4.05976796670811i | 18.9836745734912+3.06269990388089i | 38.2 | 19.2291
[34 empty] | 38.4 | 0.0001-0.991875i | 0.000001-0.0633271070855874i | 0.0243176091208656+93.3796190241238i | 19.8528960862747+0.0001i | 0.0243186091208656+93.3162919170382i | 0.473463190647573+1852.5986490173i | 19.8772146953956+93.3163919170382i | 18.9922259157224+4.04043792450554i | 18.9923259157224+3.04856292450554i | 38.4 | 19.2354
[34 empty] | 38.6 | 0.0001-0.986735751295337i | 0.000001-0.0629989873597554i | 0.0243176091208656+93.8659712065411i | 19.8528960862747+0.0001i | 0.0243186091208656+93.8029722191813i | 0.473414522617359+1862.26066248298i | 19.8772146953956+93.8030722191813i | 19.0007506060013+4.02128177385437i | 19.0008506060013+3.03454602255903i | 38.6 | 19.2416
[34 empty] | 38.8 | 0.0001-0.981649484536082i | 0.000001-0.0626742503115092i | 0.0243176091208656+94.3523233889585i | 19.8528960862747+0.0001i | 0.0243186091208656+94.289649138647i | 0.473365854925412+1871.92260879272i | 19.8772146953956+94.289749138647i | 19.0091510677469+4.00229732864155i | 19.0092510677469+3.02064784410547i | 38.8 | 19.2478
[34 empty] | 39 | 0.0001-0.976615384615384i | 0.000001-0.0623528438996553i | 0.0243176091208656+94.8386755713758i | 19.8528960862747+0.0001i | 0.0243186091208656+94.7763227274761i | 0.473317187566529+1881.58448897968i | 19.8772146953956+94.7764227274761i | 19.0174296675996+3.98348243587428i | 19.0175296675996+3.0068670512589i | 39 | 19.2538
[34 empty] | 39.2 | 0.0001-0.971632653061224i | 0.000001-0.0620347171450652i | 0.0243176091208656+95.3250277537931i | 19.8528960862747+0.0001i | 0.0243186091208656+95.262993036648i | 0.473268520535612+1891.24630405594i | 19.8772146953956+95.263093036648i | 19.025588716983+3.96483497515589i | 19.025688716983+2.99320232209467i | 39.2 | 19.2597
[34 empty] | 39.4 | 0.0001-0.966700507614213i | 0.000001-0.0617198201037197i | 0.0243176091208656+95.8113799362104i | 19.8528960862747+0.0001i | 0.0243186091208656+95.7496601161067i | 0.473219853827666+1900.90805501305i | 19.8772146953956+95.7497601161067i | 19.0336304736171+3.94635285816786i | 19.0337304736171+2.97965235055365i | 39.4 | 19.2655
[34 empty] | 39.6 | 0.0001-0.961818181818181i | 0.000001-0.0614081038405696i | 0.0243176091208656+96.2977321186277i | 19.8528960862747+0.0001i | 0.0243186091208656+96.2363240147871i | 0.473171187437798+1910.56974282249i | 19.8772146953956+96.2364240147871i | 19.0415571429837+3.92803402815767i | 19.0416571429837+2.96621584633949i | 39.6 | 19.2713
[34 empty] | 39.8 | 0.0001-0.956984924623115i | 0.000001-0.0610995204041848i | 0.0243176091208656+96.7840843010451i | 19.8528960862747+0.0001i | 0.0243186091208656+96.7229847806409i | 0.473122521361213+1920.23136843625i | 19.8772146953956+96.7230847806409i | 19.0493708797468+3.90987645943314i | 19.0494708797468+2.95289153481002i | 39.8 | 19.277
[34 empty] | 40 | 0.0001-0.952199999999999i | 0.000001-0.0607940228021639i | 0.0243176091208656+97.2704364834624i | 19.8528960862747+0.0001i | 0.0243186091208656+97.2096424606602i | 0.473073855593211+1929.89293278726i | 19.8772146953956+97.2097424606602i | 19.0570737891285+3.89187815686288i | 19.0571737891285+2.93967815686288i | 40 | 19.2826
[34 empty] | 40.2 | 0.0001-0.947462686567164i | 0.000001-0.0604915649772775i | 0.0243176091208656+97.7567886658797i | 19.8528960862747+0.0001i | 0.0243186091208656+97.6962971009024i | 0.473025190129187+1939.5544367899i | 19.8772146953956+97.6963971009024i | 19.0646679282424+3.8740371553832i | 19.0647679282424+2.92657446881604i | 40.2 | 19.2881
[34 empty] | 40.4 | 0.0001-0.942772277227722i | 0.000001-0.0601921017843207i | 0.0243176091208656+98.243140848297i | 19.8528960862747+0.0001i | 0.0243186091208656+98.1829487465127i | 0.472976524964626+1949.21588134041i | 19.8772146953956+98.1830487465127i | 19.0721553073863+3.85635151951145i | 19.0722553073863+2.91357924228373i | 40.4 | 19.2935
[34 empty] | 40.6 | 0.0001-0.938128078817733i | 0.000001-0.0598955889676491i | 0.0243176091208656+98.7294930307143i | 19.8528960862747+0.0001i | 0.0243186091208656+98.6695974417466i | 0.472927860095102+1958.87726731741i | 19.8772146953956+98.6696974417466i | 19.0795378912951+3.838819342866i | 19.0796378912951+2.90069126404827i | 40.6 | 19.2989
[34 empty] | 40.8 | 0.0001-0.933529411764705i | 0.000001-0.0596019831393764i | 0.0243176091208656+99.2158452131316i | 19.8528960862747+0.0001i | 0.0243186091208656+99.1562432299922i | 0.472879195516278+1968.53859558228i | 19.8772146953956+99.1563432299922i | 19.0868176003553+3.82143874769263i | 19.0869176003553+2.88790933592793i | 40.8 | 19.3042
[34 empty] | 41 | 0.0001-0.928975609756097i | 0.000001-0.0593112417582087i | 0.0243176091208656+99.702197395549i | 19.8528960862747+0.0001i | 0.0243186091208656+99.6428861537908i | 0.472830531223898+1978.19986697957i | 19.8772146953956+99.6429861537908i | 19.0939963117826+3.80420788439758i | 19.0940963117826+2.87523227464148i | 41 | 19.3094
[34 empty] | 41.2 | 0.0001-0.924466019417475i | 0.000001-0.059023323108897i | 0.0243176091208656+100.188549577966i | 19.8528960862747+0.0001i | 0.0243186091208656+100.129526254857i | 0.472781867213791+1987.86108233745i | 19.8772146953956+100.129626254857i | 19.1010758607637+3.78712493108733i | 19.1011758607637+2.86265891166985i | 41.2 | 19.3145
[34 empty] | 41.4 | 0.0001-0.919999999999999i | 0.000001-0.0587381862822839i | 0.0243176091208656+100.674901760384i | 19.8528960862747+0.0001i | 0.0243186091208656+100.616163574102i | 0.472733203481867+1997.52224246813i | 19.8772146953956+100.616263574102i | 19.1080580415642+3.77018809311471i | 19.1081580415642+2.85018809311471i | 41.4 | 19.3196
[34 empty] | 41.6 | 0.0001-0.915576923076922i | 0.000001-0.0584557911559268i | 0.0243176091208656+101.161253942801i | 19.8528960862747+0.0001i | 0.0243186091208656+101.102798151645i | 0.472684540024112+2007.18334816807i | 19.8772146953956+101.102898151645i | 19.1149446086017+3.75339560263212i | 19.1150446086017+2.8378186795552i | 41.6 | 19.3245
[34 empty] | 41.8 | 0.0001-0.911196172248803i | 0.000001-0.0581760983752764i | 0.0243176091208656+101.647606125218i | 19.8528960862747+0.0001i | 0.0243186091208656+101.589430026843i | 0.472635876836593+2016.84440021865i | 19.8772146953956+101.589530026843i | 19.1217372774889+3.73674571815083i | 19.1218372774889+2.82554954590203i | 41.8 | 19.3295
[34 empty] | 42 | 0.0001-0.906857142857142i | 0.000001-0.0578990693353941i | 0.0243176091208656+102.133958307636i | 19.8528960862747+0.0001i | 0.0243186091208656+102.076059238301i | 0.472587213915447+2026.50539938627i | 19.8772146953956+102.076159238301i | 19.1284377260431+3.72023672410725i | 19.1285377260431+2.81337958125011i | 42 | 19.3343
[34 empty] | 42.2 | 0.0001-0.90255924170616i | 0.000001-0.0576246661631885i | 0.0243176091208656+102.620310490053i | 19.8528960862747+0.0001i | 0.0243186091208656+102.56268582389i | 0.472538551256888+2036.16634642279i | 19.8772146953956+102.56278582389i | 19.1350475952673+3.70386693043588i | 19.1351475952673+2.80130768872972i | 42.2 | 19.3391
[34 empty] | 42.4 | 0.0001-0.898301886792452i | 0.000001-0.0573528517001546i | 0.0243176091208656+103.10666267247i | 19.8528960862747+0.0001i | 0.0243186091208656+103.04930982077i | 0.4724898888572+2045.82724206593i | 19.8772146953956+103.04940982077i | 19.1415684903019+3.68763467214831i | 19.1416684903019+2.78933278535586i | 42.4 | 19.3438
[34 empty] | 42.6 | 0.0001-0.894084507042252i | 0.000001-0.0570835894855999i | 0.0243176091208656+103.593014854888i | 19.8528960862747+0.0001i | 0.0243186091208656+103.535931265402i | 0.472441226712737+2055.48808703957i | 19.8772146953956+103.536031265402i | 19.1480019813478+3.67153830891939i | 19.1481019813478+2.77745380187714i | 42.6 | 19.3485
[34 empty] | 42.8 | 0.0001-0.889906542056074i | 0.000001-0.05681684374034i | 0.0243176091208656+104.079367037305i | 19.8528960862747+0.0001i | 0.0243186091208656+104.022550193565i | 0.47239256481992+2065.148882054i | 19.8772146953956+104.022650193565i | 19.1543496045626+3.65557622467938i | 19.1544496045626+2.76566968262331i | 42.8 | 19.3531
[34 empty] | 43 | 0.0001-0.885767441860464i | 0.000001-0.0565525793508501i | 0.0243176091208656+104.565719219722i | 19.8528960862747+0.0001i | 0.0243186091208656+104.509166640371i | 0.47234390317524+2074.80962780631i | 19.8772146953956+104.509266640371i | 19.1606128629304+3.63974682721302i | 19.1607128629304+2.75397938535256i | 43 | 19.3576
[34 empty] | 43.2 | 0.0001-0.881666666666665i | 0.000001-0.0562907618538554i | 0.0243176091208656+105.052071402139i | 19.8528960862747+0.0001i | 0.0243186091208656+104.995780640285i | 0.472295241775248+2084.47032498073i | 19.8772146953956+104.995880640285i | 19.1667932271063+3.62404854776442i | 19.1668932271063+2.74238188109776i | 43.2 | 19.3621
[34 empty] | 43.4 | 0.0001-0.877603686635943i | 0.000001-0.0560313574213492i | 0.0243176091208656+105.538423584557i | 19.8528960862747+0.0001i | 0.0243186091208656+105.482392227136i | 0.472246580616563+2094.13097424886i | 19.8772146953956+105.482492227136i | 19.1728921362364+3.60847984064883i | 19.1729921362364+2.73087615401289i | 43.4 | 19.3665
[34 empty] | 43.6 | 0.0001-0.873577981651375i | 0.000001-0.0557743328460219i | 0.0243176091208656+106.024775766974i | 19.8528960862747+0.0001i | 0.0243186091208656+105.969001434128i | 0.472197919695864+2103.7915762699i | 19.8772146953956+105.969101434128i | 19.1789109987534+3.59303918287059i | 19.1790109987534+2.71946120121921i | 43.6 | 19.3709
[34 empty] | 43.8 | 0.0001-0.869589041095889i | 0.000001-0.0555196555270902i | 0.0243176091208656+106.511127949391i | 19.8528960862747+0.0001i | 0.0243186091208656+106.455608293864i | 0.472149259009891+2113.45213169111i | 19.8772146953956+106.455708293864i | 19.1848511931498+3.57772507374692i | 19.1849511931498+2.70813603265103i | 43.8 | 19.3751
[34 empty] | 44 | 0.0001-0.865636363636362i | 0.000001-0.0552672934565126i | 0.0243176091208656+106.997480131809i | 19.8528960862747+0.0001i | 0.0243186091208656+106.942212838352i | 0.472100598555442+2123.11264114794i | 19.8772146953956+106.942312838352i | 19.1907140687286+3.56253603453844i | 19.1908140687286+2.69689967090208i | 44 | 19.3794
[34 empty] | 44.2 | 0.0001-0.861719457013573i | 0.000001-0.0550172152055781i | 0.0243176091208656+107.483832314226i | 19.8528960862747+0.0001i | 0.0243186091208656+107.42881509902i | 0.472051938329375+2132.77310526432i | 19.8772146953956+107.42891509902i | 19.1965009463324+3.54747060808548i | 19.1966009463324+2.68575115107191i | 44.2 | 19.3836
[34 empty] | 44.4 | 0.0001-0.857837837837836i | 0.000001-0.0547693899118593i | 0.0243176091208656+107.970184496643i | 19.8528960862747+0.0001i | 0.0243186091208656+107.915415106731i | 0.472003278328604+2142.43352465299i | 19.8772146953956+107.915515106731i | 19.2022131190519+3.53252735845052i | 19.2023131190519+2.67468952061268i | 44.4 | 19.3877
[34 empty] | 44.6 | 0.0001-0.853991031390133i | 0.000001-0.0545237872665146i | 0.0243176091208656+108.456536679061i | 19.8528960862747+0.0001i | 0.0243186091208656+108.402012891794i | 0.471954618550098+2152.09389991566i | 19.8772146953956+108.402112891794i | 19.2078518529134+3.51770487056648i | 19.2079518529134+2.66371383917635i | 44.6 | 19.3918
[34 empty] | 44.8 | 0.0001-0.85017857142857i | 0.000001-0.054280377501932i | 0.0243176091208656+108.942888861478i | 19.8528960862747+0.0001i | 0.0243186091208656+108.888608483976i | 0.471905958990879+2161.75423164329i | 19.8772146953956+108.888708483976i | 19.2134183875478+3.50300174989118i | 19.2135183875478+2.65282317846261i | 44.8 | 19.3958
[34 empty] | 45 | 0.0001-0.846399999999998i | 0.000001-0.0540391313797012i | 0.0243176091208656+109.429241043895i | 19.8528960862747+0.0001i | 0.0243186091208656+109.375201912515i | 0.471857299648025+2171.41452041634i | 19.8772146953956+109.375301912515i | 19.21891393684+3.48841662206735i | 19.21901393684+2.64201662206735i | 45 | 19.3998
[34 empty] | 45.2 | 0.0001-0.842654867256635i | 0.000001-0.053800020178906i | 0.0243176091208656+109.915593226313i | 19.8528960862747+0.0001i | 0.0243186091208656+109.861793206134i | 0.471808640518664+2181.07476680504i | 19.8772146953956+109.861893206134i | 19.2243396895602+3.47394813258849i | 19.2244396895602+2.63129326533186i | 45.2 | 19.4037
[34 empty] | 45.4 | 0.0001-0.838942731277531i | 0.000001-0.0535630156847258i | 0.0243176091208656+110.40194540873i | 19.8528960862747+0.0001i | 0.0243186091208656+110.348382393045i | 0.471759981599972+2190.73497136949i | 19.8772146953956+110.348482393045i | 19.2296968099774+3.45959494647066i | 19.2297968099774+2.62065221519313i | 45.4 | 19.4075
[34 empty] | 45.6 | 0.0001-0.835263157894735i | 0.000001-0.0533280901773367i | 0.0243176091208656+110.888297591147i | 19.8528960862747+0.0001i | 0.0243186091208656+110.83496950097i | 0.47171132288918+2200.39513466004i | 19.8772146953956+110.83506950097i | 19.2349864384555+3.44535574792933i | 19.2350864384555+2.6100925900346i | 45.6 | 19.4114
[34 empty] | 45.8 | 0.0001-0.831615720524016i | 0.000001-0.0530952164211037i | 0.0243176091208656+111.374649773565i | 19.8528960862747+0.0001i | 0.0243186091208656+111.321554557144i | 0.471662664383563+2210.0552572174i | 19.8772146953956+111.321654557144i | 19.2402096920334+3.43122924006238i | 19.2403096920334+2.59961351953836i | 45.8 | 19.4151
[34 empty] | 46 | 0.0001-0.827999999999998i | 0.000001-0.0528643676540555i | 0.0243176091208656+111.861001955982i | 19.8528960862747+0.0001i | 0.0243186091208656+111.808137588328i | 0.471614006080444+2219.71533957284i | 19.8772146953956+111.808237588328i | 19.2453676649881+3.41721414453811i | 19.2454676649881+2.58921414453811i | 46 | 19.4189
[34 empty] | 46.2 | 0.0001-0.824415584415582i | 0.000001-0.052635517577631i | 0.0243176091208656+112.347354138399i | 19.8528960862747+0.0001i | 0.0243186091208656+112.294718620821i | 0.471565347977195+2229.37538224848i | 19.8772146953956+112.294818620821i | 19.2504614293828+3.40330920128879i | 19.2505614293828+2.57889361687321i | 46.2 | 19.4225
[34 empty] | 46.4 | 0.0001-0.820862068965515i | 0.000001-0.0524086403466929i | 0.0243176091208656+112.833706320817i | 19.8528960862747+0.0001i | 0.0243186091208656+112.78129768047i | 0.47151669007123+2239.03538575745i | 19.8772146953956+112.78139768047i | 19.2554920355996+3.38951316820947i | 19.2555920355996+2.56865109924395i | 46.4 | 19.4262
[34 empty] | 46.6 | 0.0001-0.817339055793989i | 0.000001-0.0521837105597972i | 0.0243176091208656+113.320058503234i | 19.8528960862747+0.0001i | 0.0243186091208656+113.267874792674i | 0.47146803236001+2248.69535060399i | 19.8772146953956+113.267974792674i | 19.2604605128578+3.3758248208622i | 19.2605605128578+2.55848576506821i | 46.6 | 19.4297
[34 empty] | 46.8 | 0.0001-0.813846153846152i | 0.000001-0.0519607032497126i | 0.0243176091208656+113.806410685651i | 19.8528960862747+0.0001i | 0.0243186091208656+113.754449982401i | 0.471419374841037+2258.3552772838i | 19.8772146953956+113.754549982401i | 19.2653678697176+3.36224295218507i | 19.2654678697176+2.54839679833892i | 46.8 | 19.4333
[34 empty] | 47 | 0.0001-0.810382978723402i | 0.000001-0.0517395938741819i | 0.0243176091208656+114.292762868069i | 19.8528960862747+0.0001i | 0.0243186091208656+114.241023274195i | 0.471370717511857+2268.01516628414i | 19.8772146953956+114.241123274195i | 19.2702150945704+3.34876637220646i | 19.2703150945704+2.53838339348306i | 47 | 19.4368
[34 empty] | 47.2 | 0.0001-0.806949152542371i | 0.000001-0.0515203583069185i | 0.0243176091208656+114.779115050486i | 19.8528960862747+0.0001i | 0.0243186091208656+114.727594692179i | 0.471322060370059+2277.67501808393i | 19.8772146953956+114.727694692179i | 19.2750031561153+3.33539390776451i | 19.2751031561153+2.52844475522214i | 47.2 | 19.4402
[34 empty] | 47.4 | 0.0001-0.803544303797466i | 0.000001-0.0513029728288302i | 0.0243176091208656+115.265467232903i | 19.8528960862747+0.0001i | 0.0243186091208656+115.214164260074i | 0.47127340341327+2287.33483315409i | 19.8772146953956+115.214264260074i | 19.279733003823+3.32212440223098i | 19.279833003823+2.51858009843351i | 47.4 | 19.4436
[34 empty] | 47.6 | 0.0001-0.800168067226889i | 0.000001-0.0510874141194653i | 0.0243176091208656+115.75181941532i | 19.8528960862747+0.0001i | 0.0243186091208656+115.700732001201i | 0.471224746639157+2296.99461195762i | 19.8772146953956+115.700832001201i | 19.2844055683874+3.30895671524044i | 19.2845055683874+2.50878864801355i | 47.6 | 19.447
[34 empty] | 47.8 | 0.0001-0.796820083682006i | 0.000001-0.0508736592486726i | 0.0243176091208656+116.238171597738i | 19.8528960862747+0.0001i | 0.0243186091208656+116.187297938489i | 0.471176090045428+2306.65435494972i | 19.8772146953956+116.187397938489i | 19.2890217621642+3.29588972242398i | 19.2891217621642+2.49906963874197i | 47.8 | 19.4503
[34 empty] | 48 | 0.0001-0.793499999999998i | 0.000001-0.0506616856684698i | 0.0243176091208656+116.724523780155i | 19.8528960862747+0.0001i | 0.0243186091208656+116.673862094487i | 0.471127433629828+2316.31406257806i | 19.8772146953956+116.673962094487i | 19.2935824795988+3.28292231514761i | 19.2936824795988+2.48942231514761i | 48 | 19.4536
[34 empty] | 48.2 | 0.0001-0.790207468879666i | 0.000001-0.0504514712051152i | 0.0243176091208656+117.210875962572i | 19.8528960862747+0.0001i | 0.0243186091208656+117.160424491367i | 0.47107877739014+2325.9737352828i | 19.8772146953956+117.160524491367i | 19.2980885976412+3.27005340025531i | 19.2981885976412+2.47984593137564i | 48.2 | 19.4569
[34 empty] | 48.4 | 0.0001-0.786942148760328i | 0.000001-0.050242994051375i | 0.0243176091208656+117.69722814499i | 19.8528960862747+0.0001i | 0.0243186091208656+117.646985150939i | 0.471030121324183+2335.63337349696i | 19.8772146953956+117.647085150939i | 19.3025409761523+3.25728189981652i | 19.3026409761523+2.47033975105619i | 48.4 | 19.4601
[34 empty] | 48.6 | 0.0001-0.783703703703701i | 0.000001-0.0500362327589825i | 0.0243176091208656+118.183580327407i | 19.8528960862747+0.0001i | 0.0243186091208656+118.133544094648i | 0.470981465429812+2345.29297764626i | 19.8772146953956+118.133644094648i | 19.3069404582962+3.24460675087825i | 19.3070404582962+2.46090304717455i | 48.6 | 19.4632
[34 empty] | 48.8 | 0.0001-0.780491803278686i | 0.000001-0.0498311662312818i | 0.0243176091208656+118.669932509824i | 19.8528960862747+0.0001i | 0.0243186091208656+118.620101343593i | 0.470932809704918+2354.95254814959i | 19.8772146953956+118.620201343593i | 19.311287870925+3.2320269052213i | 19.311387870925+2.45153510194261i | 48.8 | 19.4664
[34 empty] | 49 | 0.0001-0.777306122448977i | 0.000001-0.049627773716052i | 0.0243176091208656+119.156284692242i | 19.8528960862747+0.0001i | 0.0243186091208656+119.106656918526i | 0.470884154147424+2364.61208541893i | 19.8772146953956+119.106756918526i | 19.3155840249517+3.21954132912107i | 19.3156840249517+2.44223520667209i | 49 | 19.4695
[34 empty] | 49.2 | 0.0001-0.774146341463412i | 0.000001-0.0494260347985071i | 0.0243176091208656+119.642636874659i | 19.8528960862747+0.0001i | 0.0243186091208656+119.593210839861i | 0.470835498755291+2374.27158985956i | 19.8772146953956+119.593310839861i | 19.319829715714+3.20714900311244i | 19.319929715714+2.43300266164903i | 49.2 | 19.4725
[34 empty] | 49.4 | 0.0001-0.771012145748985i | 0.000001-0.0492259293944646i | 0.0243176091208656+120.128989057076i | 19.8528960862747+0.0001i | 0.0243186091208656+120.079763127682i | 0.470786843526509+2383.93106187021i | 19.8772146953956+120.079863127682i | 19.3240257233282+3.19484892175877i | 19.3241257233282+2.42383677600978i | 49.4 | 19.4755
[34 empty] | 49.6 | 0.0001-0.767903225806449i | 0.000001-0.0490274377436804i | 0.0243176091208656+120.615341239494i | 19.8528960862747+0.0001i | 0.0243186091208656+120.56631380175i | 0.470738188459102+2393.59050184319i | 19.8772146953956+120.56641380175i | 19.3281728130341+3.18264009342508i | 19.3282728130341+2.41473686761863i | 49.6 | 19.4785
[34 empty] | 49.8 | 0.0001-0.764819277108431i | 0.000001-0.0488305404033444i | 0.0243176091208656+121.101693421911i | 19.8528960862747+0.0001i | 0.0243186091208656+121.052862881508i | 0.470689533551126+2403.2499101645i | 19.8772146953956+121.052962881508i | 19.3322717355309+3.17052154005521i | 19.3323717355309+2.40570226294678i | 49.8 | 19.4815
[34 empty] | 50 | 0.0001-0.761759999999998i | 0.000001-0.048635218241731i | 0.0243176091208656+121.588045604328i | 19.8528960862747+0.0001i | 0.0243186091208656+121.539410386086i | 0.470640878800668+2412.90928721392i | 19.8772146953956+121.539510386086i | 19.336323227304+3.15849229695295i | 19.336423227304+2.39673229695295i | 50 | 19.4844
(mH)
𝐻=𝑋_𝐿/2𝜋𝑓×1000 (mH)
(kvar/phase)
〖𝑄_(𝑀𝐴𝐼𝑁 𝑅𝐴𝑇𝐸𝐷 𝑃𝐸𝑅 𝑃𝐻𝐴𝑆𝐸) =(𝑉_(𝐶𝐴𝑃 𝑀𝐴𝐼𝑁 𝑅𝐴𝑇𝐼𝑁𝐺) )^2/𝑋_(𝐶−𝑀𝐴𝐼𝑁) ×1000〗_(kvar/phase)
(amps)
𝐼_(𝑅𝐴𝑇𝐸𝐷 𝐹𝑈𝑁𝐷𝐴𝑀𝐸𝑁𝑇𝐴𝐿)= 𝑄_𝑒𝑓𝑓/(1.73×〖〖𝑘𝑉〗_𝐿𝐿𝑆𝑌𝑆〗^ ) (amps)
/ 1000 (kV)
V_(CAP MAIN FUNDAMENTAL VOLTAGE)=I_(MAIN FUNDAMENTAL)× X_(C−MAIN)/ 1000 (kV)
𝑉_(𝐶𝐴𝑃 𝐻𝐴𝑅𝑀𝑂𝑁𝐼𝐶 𝑉𝑂𝐿𝑇𝐴𝐺𝐸)=𝑋_𝐶/𝑛×𝐼_𝑛
/1000 (kV)
𝑉_(𝐶𝐴𝑃 𝑀𝐴𝐼𝑁 𝑅𝑀𝑆 𝑉𝑂𝐿𝑇𝐴𝐺𝐸)=√(∑_(𝑛=1)^𝑛▒〖𝑉_(𝐶𝐴𝑃 𝐻𝐴𝑅𝑀𝑂𝑁𝐼𝐶 𝑉𝑂𝐿𝑇𝐴𝐺𝐸 (𝑉𝑂𝐿𝑇𝑆))〗^2 ) /1000 (kV)
𝑉_(𝐶𝐴𝑃 𝑀𝐴𝐼𝑁 𝑃𝐸𝐴𝐾 𝑉𝑂𝐿𝑇𝐴𝐺𝐸)=1.414 ×∑_(𝑛=1)^𝑛▒〖𝑉_(𝐶𝐴𝑃 𝐻𝐴𝑅𝑀𝑂𝑁𝐼𝐶 𝑉𝑂𝐿𝑇𝐴𝐺𝐸)〗^
(amps/capacitor)
𝐼_(𝐶𝐴𝑃 𝑀𝐴𝐼𝑁)= 𝐼_(𝑅𝐴𝑇𝐸𝐷 𝐹𝑈𝑁𝐷𝐴𝑀𝐸𝑁𝑇𝐴𝐿)/𝑁_𝑀𝐴𝐼𝑁 (amps/capacitor)
/N
𝐼_(𝐶𝐴𝑃 𝑀𝐴𝐼𝑁 𝑅𝑀𝑆 𝐶𝑈𝑅𝑅𝐸𝑁𝑇)=√(∑_(𝑛=1)^𝑛▒〖𝐼_𝑛^ 〗_^2 ) /N
𝐼_(𝐹𝐼𝐿𝑇𝐸𝑅 𝑅𝑀𝑆 𝐶𝑈𝑅𝑅𝐸𝑁𝑇)=√(∑_(𝑛=1)^𝑛▒〖𝐼_𝑛^ 〗_^2 )
(ohms/phase)
𝑅=𝑋_𝐿×𝐷𝐹×ℎ (ohms/phase)
𝐼_(𝑅𝐸𝑆𝐼𝑆𝑇𝑂𝑅 (𝑛))=𝑋_𝐿/〖𝑅+𝑗𝑋〗_𝐿 ×𝐼_𝑛
𝐼_(𝑅𝐸𝐴𝐶𝑇𝑂𝑅 (𝑛))=𝑅/〖𝑅+𝑗𝑋〗_𝐿 ×𝐼_𝑛
(kW/Phase)
𝑅_𝑊=√(∑_(𝑛=1)^𝑛▒〖〖𝐼_𝑛^ 〗_^2×𝑅〗)/1000 (kW/Phase)
(ohms)
𝑋_(𝐶−𝐴𝑈𝑋)=𝑋_𝐿 (ohms)
(ohms)
〖𝑋_𝐿 =𝑥_𝑒𝑓𝑓/(〖(ℎ〗^2−1))〗_(ohms)
(ohms)
𝑋_(𝐶−𝑀𝐴𝐼𝑁)=𝑋_𝑒𝑓𝑓 (ohms)
(kvar/phase)
〖𝑄_(𝐴𝑈𝑋 𝑅𝐴𝑇𝐸𝐷 𝑃𝐸𝑅 𝑃𝐻𝐴𝑆𝐸) =(𝑉_(𝐶𝐴𝑃 𝐴𝑈𝑋 𝑅𝐴𝑇𝐼𝑁𝐺) )^2/𝑋_(𝐶−𝐴𝑈𝑋) ×1000〗_(kvar/phase)
𝐼_(𝐶𝐴𝑃 𝐴𝑈𝑋)= 𝐼_(𝑅𝐴𝑇𝐸𝐷 𝐹𝑈𝑁𝐷𝐴𝑀𝐸𝑁𝑇𝐴𝐿)/𝑁_𝐴𝑈𝑋
V_(CAP AUX FUNDAMENTAL VOLTAGE)=I_(AUX UNDAMENTAL)× X_(C−AUX)
(ohms)
𝑋_𝑒𝑓𝑓= 〖〖𝑘𝑉〗_𝐿𝐿𝑆𝑌𝑆〗^2/(𝑄_𝑒𝑓𝑓 (𝑀𝑉𝐴𝑅)) (ohms)
/1000
𝑉_(𝐶𝐴𝑃 𝐴𝑈𝑋 𝑅𝑀𝑆 𝑉𝑂𝐿𝑇𝐴𝐺𝐸)=√(∑_(𝑛=1)^𝑛▒〖𝑉_(𝐶𝐴𝑃 𝐻𝐴𝑅𝑀𝑂𝑁𝐼𝐶 𝑉𝑂𝐿𝑇𝐴𝐺𝐸 (𝑉𝑂𝐿𝑇𝑆))〗^2 ) /1000
𝑉_(𝐶𝐴𝑃 𝐴𝑈𝑋 𝑃𝐸𝐴𝐾 𝑉𝑂𝐿𝑇𝐴𝐺𝐸)=1.414 ×∑_(𝑛=1)^𝑛▒〖𝑉_(𝐶𝐴𝑃 𝐻𝐴𝑅𝑀𝑂𝑁𝐼𝐶 𝑉𝑂𝐿𝑇𝐴𝐺𝐸)〗^
/N
𝐼_(𝐶𝐴𝑃 𝐴𝑈𝑋 𝑅𝑀𝑆 𝐶𝑈𝑅𝑅𝐸𝑁𝑇)=√(∑_(𝑛=1)^𝑛▒〖𝐼_𝑛^ 〗_^2 ) /N
𝐷𝐹= 𝑅/(ℎ×𝑋_𝐿 )
(amps)
𝐼_(𝑀𝐴𝐼𝑁 𝐹𝑈𝑆𝐸)≥ 𝐼_(𝐶𝐴𝑃 𝑀𝐴𝐼𝑁)×1.8 (amps)
𝐼_(𝐴𝑈𝑋 𝐹𝑈𝑆𝐸)≥ 𝐼_(𝐶𝐴𝑃 𝐴𝑈𝑋)×1.8
/1000
𝑄_( 𝐶𝐴𝑃𝐴𝐶𝐼𝑇𝑂𝑅)=∑_(𝑛=1)^𝑛▒〖〖𝑋_𝑐/𝑛 𝑥 𝐼〗_𝑛^ 〗_^2 /1000

## Notch Filter Delta Connection
Rev: 10-7-2019 | [34 empty] | PLOT (ohms) |  |  | (res branch) | (aux branch) | product of res branch and aux branch | sum of res branch and aux branch | power over sum rule of aux and res branch | add main cap in |  |  | SD - Standard Duty Capacitors, with -40C to +55C Temperature Rating
[34 empty] | HARM # | Xc main | Xc aux | XL (inductance) | Resistance | XCAUX + XL | [6 empty] | HD- Heavy Duty Capacitors, with -40C to +55C Temperature Rating
Northeast Power Systems, Inc. | [33 empty] | 1 | 0.0001-18.1640126984127i | 0.000000001-0.00000000000000001i | 0.00858412698412699+0.858412698412699i | 9999999999+9999999i | 0.00858412798412699+0.858412698412699i | 77257153.7069715+8584212824.53983i | 9999999999.00858+9999999.8584127i | 0.00858412805780532+0.858412698411152i | 0.00868412805780532-17.3056000000016i | 1 | 17.3056 | EXD - Extreme Duty Capacitors, with -50C to +55C Temperature Rating
66 Carey Road, Queensbury, NY |  |  |  |  | Phone: (518) 792-4776 Fax: (518) 792-5767 www.nepsi.com | [28 empty] | 1.2 | 0.0001-15.1366772486773i | 0.000000001-0.00000000000000001i | 0.00858412698412699+1.03009523809524i | 9999999999+9999999i | 0.00858412798412699+1.03009523809524i | 75540328.4818286+10301038221.1936i | 9999999999.00858+10000000.0300952i | 0.00858412809022737+1.03009523809337i | 0.00868412809022737-14.1065820105839i | 1.2 | 14.1066
[34 empty] | 1.4 | 0.0001-12.9742947845805i | 0.000000001-0.00000000000000001i | 0.00858412698412699+1.20177777777778i | 9999999999+9999999i | 0.00858412798412699+1.20177777777778i | 73823503.2566857+12017863617.8473i | 9999999999.00858+10000000.2017778i | 0.0085841281285444+1.20177777777557i | 0.0086841281285444-11.7725170068049i | 1.4 | 11.7725
FILTER BANK DESIGN CALCULATIONS - NOTCH FILTER DESIGN | [10 empty] | REVERSE CALCULATION USING C AND L | [22 empty] | 1.6 | 0.0001-11.3525079365079i | 0.000000001-0.00000000000000001i | 0.00858412698412699+1.37346031746032i | 9999999999+9999999i | 0.00858412798412699+1.37346031746032i | 72106678.0315429+13734689014.501i | 9999999999.00858+10000000.3734603i | 0.0085841281727564+1.37346031745777i | 0.0086841281727564-9.97904761905013i | 1.6 | 9.9791
[34 empty] | 1.8 | 0.0001-10.0911181657848i | 0.000000001-0.00000000000000001i | 0.00858412698412699+1.54514285714286i | 9999999999+9999999i | 0.00858412798412699+1.54514285714286i | 70389852.8064+15451514411.1547i | 9999999999.00858+10000000.5451429i | 0.00858412822286338+1.54514285713997i | 0.00868412822286338-8.54597530864483i | 1.8 | 8.546
kVLLsys (System Line-to-Line Voltage Rating) |  | 4.16 | kV |  |  | Job Name: | Enter Job Name |  |  |  | CAPACITANCE (µf) | 2.13 | (µf) | [20 empty] | 2 | 0.0001-9.08200634920635i | 0.000000001-0.00000000000000001i | 0.00858412698412699+1.7168253968254i | 9999999999+9999999i | 0.00858412798412699+1.7168253968254i | 68673027.5812572+17168339807.8084i | 9999999999.00858+10000000.7168254i | 0.00858412827886533+1.71682539682216i | 0.00868412827886533-7.36518095238419i | 2 | 7.3652
Qeff (3-Phase Output Rating of Filter) |  | 1000 | kvar |  |  | Stage/Branch Name | Branch/Stage # |  |  |  | INDUCTANCE (mH) | 149.7 | mH | [20 empty] | 2.2 | 0.0001-8.25636940836941i | 0.000000001-0.00000000000000001i | 0.00858412698412699+1.88850793650794i | 9999999999+9999999i | 0.00858412798412699+1.88850793650794i | 66956202.3561143+18885165204.4621i | 9999999999.00858+10000000.8885079i | 0.00858412834076224+1.88850793650434i | 0.00868412834076224-6.36786147186507i | 2.2 | 6.3679
h (Tuning Point of Filter) |  | 4.6 | (harmonic #) | [7 empty] | XL (Ohms) | 56.4339 | Ohms | [20 empty] | 2.4 | 0.0001-7.56833862433863i | 0.000000001-0.00000000000000001i | 0.00858412698412699+2.06019047619048i | 9999999999+9999999i | 0.00858412798412699+2.06019047619048i | 65239377.1309714+20601990601.1159i | 9999999999.00858+10000001.0601905i | 0.00858412840855415+2.06019047618652i | 0.00868412840855415-5.50814814815211i | 2.4 | 5.5082
f (System Frequency) |  | 60 | (HZ) | [7 empty] | Xc (Ohms) | 1245.3806 | Ohms | [20 empty] | 2.6 | 0.0001-6.98615873015873i | 0.000000001-0.00000000000000001i | 0.00858412698412699+2.23187301587302i | 9999999999+9999999i | 0.00858412798412699+2.23187301587302i | 63522551.9058286+22318815997.7696i | 9999999999.00858+10000001.231873i | 0.00858412848224101+2.23187301586869i | 0.00868412848224101-4.75428571429004i | 2.6 | 4.7543
hFrequency |  | 276 | Hz | [7 empty] | h (Tuning Point) | 4.6977 | [21 empty] | 2.8 | 0.0001-6.48714739229025i | 0.000000001-0.00000000000000001i | 0.00858412698412699+2.40355555555556i | 9999999999+9999999i | 0.00858412798412699+2.40355555555556i | 61805726.6806857+24035641394.4233i | 9999999999.00858+10000001.4035556i | 0.00858412856182286+2.40355555555086i | 0.00868412856182286-4.08359183673939i | 2.8 | 4.0836
Xeff (effective reactance of Filter Bank) |  | 17.3056 | Ohms | [30 empty] | 3 | 0.0001-6.0546708994709i | 0.000000001-0.00000000000000001i | 0.00858412698412699+2.5752380952381i | 9999999999+9999999i | 0.00858412798412699+2.5752380952381i | 60088901.4555429+25752466791.077i | 9999999999.00858+10000001.5752381i | 0.00858412864729967+2.57523809523301i | 0.00868412864729967-3.47943280423789i | 3 | 3.4794
IRATED FUNDAMENTAL (outside of delta) |  | 138.9506 | amps | [7 empty] | Qeff (Delta-Connection) | 0.043666 | MVAR | [20 empty] | 3.2 | 0.0001-5.67625396825397i | 0.000000001-0.00000000000000001i | 0.00858412698412699+2.74692063492064i | 9999999999+9999999i | 0.00858412798412699+2.74692063492064i | 58372076.2304+27469292187.7307i | 9999999999.00858+10000001.7469206i | 0.00858412873867144+2.74692063491517i | 0.00868412873867144-2.9293333333388i | 3.2 | 2.9293
IFILTER RMS CURRENT (outside of delta) |  | 143.227 | amps | [30 empty] | 3.4 | 0.0001-5.34235667600373i | 0.000000001-0.00000000000000001i | 0.00858412698412699+2.91860317460318i | 9999999999+9999999i | 0.00858412798412699+2.91860317460318i | 56655251.0052571+29186117584.3845i | 9999999999.00858+10000001.9186032i | 0.00858412883593822+2.91860317459732i | 0.00868412883593822-2.42375350140641i | 3.4 | 2.4238
[11 empty] | CAPACITANCE CALCULATOR | [22 empty] | 3.6 | 0.0001-5.04555908289242i | 0.000000001-0.00000000000000001i | 0.00858412698412699+3.09028571428572i | 9999999999+9999999i | 0.00858412798412699+3.09028571428572i | 54938425.7801143+30902942981.0382i | 9999999999.00858+10000002.0902857i | 0.00858412893909995+3.09028571427946i | 0.00868412893909995-1.95527336861296i | 3.6 | 1.9553
IRATED FUNDAMENTAL (INSIDE DELTA) |  | 80.2301 | amps | [30 empty] | 3.8 | 0.0001-4.78000334168755i | 0.000000001-0.00000000000000001i | 0.00858412698412699+3.26196825396826i | 9999999999+9999999i | 0.00858412798412699+3.26196825396826i | 53221600.5549714+32619768377.6919i | 9999999999.00858+10000002.2619683i | 0.00858412904815667+3.2619682539616i | 0.00868412904815667-1.51803508772595i | 3.8 | 1.5181
IFILTER RMS CURRENT (INSIDE DELTA) |  | 82.6993 | amps | [7 empty] | CAPACITOR KVAR | 438 | kvar | [20 empty] | 4 | 0.0001-4.54100317460317i | 0.000000001-0.00000000000000001i | 0.00858412698412699+3.4336507936508i | 9999999999+9999999i | 0.00858412798412699+3.4336507936508i | 51504775.3298286+34336593774.3456i | 9999999999.00858+10000002.4336508i | 0.00858412916310834+3.43365079364373i | 0.00868412916310834-1.10735238095944i | 4 | 1.1074
[11 empty] | CAPACITOR FREQUENCY | 60 | Hertz | [20 empty] | 4.2 | 0.0001-4.3247649281935i | 0.000000001-0.00000000000000001i | 0.00858412698412699+3.60533333333334i | 9999999999+9999999i | 0.00858412798412699+3.60533333333334i | 49787950.1046857+36053419170.9993i | 9999999999.00858+10000002.6053333i | 0.00858412928395497+3.60533333332585i | 0.00868412928395497-0.71943159486765i | 4.2 | 0.71948
Xc (Y-EQUIVALENT) |  | 18.164 | Ohms | [7 empty] | CAPACITOR VOLTAGE (kV) | 4.16 | kV | [20 empty] | 4.4 | 0.0001-4.1281847041847i | 0.000000001-0.00000000000000001i | 0.00858412698412699+3.77701587301588i | 9999999999+9999999i | 0.00858412798412699+3.77701587301588i | 48071124.8795428+37770244567.653i | 9999999999.00858+10000002.7770159i | 0.00858412941069661+3.77701587300797i | 0.00868412941069661-0.35116883117673i | 4.4 | 0.35128
Xc (DELTA CONNECTION) |  | 54.492 | Ohms | [7 empty] | CAPACITANCE (µf) | 67.14 | (µf) | [20 empty] | 4.6 | 0.0001-3.94869841269841i | 0.000000001-0.00000000000000001i | 0.00858412698412699+3.94869841269842i | 9999999999+9999999i | 0.00858412798412699+3.94869841269842i | 46354299.6544+39487069964.3068i | 9999999999.00858+10000002.9486984i | 0.00858412954333321+3.94869841269009i | 0.00868412954333321-8.32001134654092E-12i | 4.6 | 0.0086841
[9 empty] | Capacitance (per phase): | 48.68 micro-farads/Phase | Xc (Ohms) | 39.5105 | Ohms | [20 empty] | 4.8 | 0.0001-3.78416931216931i | 0.000000001-0.00000000000000001i | 0.00858412698412699+4.12038095238096i | 9999999999+9999999i | 0.00858412798412699+4.12038095238096i | 44637474.4292571+41203895360.9605i | 9999999999.00858+10000003.120381i | 0.00858412968186479+4.12038095237219i | 0.00868412968186479+0.33621164020288i | 4.8 | 0.33632
XL (Inductive reactance of reactor at system frequency, Y-Equivalent) |  | 0.85841 | ohms | [7 empty] | RATED CURRENT | 105.2885 | AMPS | [20 empty] | 5 | 0.0001-3.63280253968254i | 0.000000001-0.00000000000000001i | 0.00858412698412699+4.2920634920635i | 9999999999+9999999i | 0.00858412798412699+4.2920634920635i | 42920649.2041143+42920720757.6142i | 9999999999.00858+10000003.2920635i | 0.00858412982629133+4.29206349205429i | 0.00868412982629133+0.659260952371751i | 5 | 0.65932
XL (Inductive reactance of reactor at system frequency, Delta Connection) |  | 2.5752 | Ohms | [30 empty] | 5.2 | 0.0001-3.49307936507936i | 0.000000001-0.00000000000000001i | 0.00858412698412699+4.46374603174603i | 9999999999+9999999i | 0.00858412798412699+4.46374603174603i | 41203823.9789715+44637546154.2678i | 9999999999.00858+10000003.463746i | 0.00858412997661282+4.46374603173637i | 0.00868412997661282+0.970666666657011i | 5.2 | 0.97071
H (Inductance of Reactor, Y-Equivalent) |  | 2.2771 | mH | [30 empty] | 5.4 | 0.0001-3.36370605526161i | 0.000000001-0.00000000000000001i | 0.00858412698412699+4.63542857142857i | 9999999999+9999999i | 0.00858412798412699+4.63542857142857i | 39486998.7538286+46354371550.9215i | 9999999999.00858+10000003.6354286i | 0.00858413013282933+4.63542857141846i | 0.00868413013282933+1.27172251615685i | 5.4 | 1.2718
H (Inductance of Reactor, Delta Connection) |  | 6.8312 | mH | [32 empty] | 0.000000001-0.00000000000000001i
XX/R RATIO (X/R OF IRON-CORE REACTOR AT FUNDAMENTAL FREQUENCY) |  | 100 | Typically Near 100 | [30 empty] | 5.6 | 0.0001-3.24357369614512i | 0.000000001-0.00000000000000001i | 0.00858412698412699+4.80711111111111i | 9999999999+9999999i | 0.00858412798412699+4.80711111111111i | 37770173.5286858+48071196947.5752i | 9999999999.00858+10000003.8071111i | 0.00858413029494078+4.80711111110054i | 0.00868413029494078+1.56353741495542i | 5.6 | 1.5636
[34 empty] | 5.8 | 0.0001-3.13172632731253i | 0.000000001-0.00000000000000001i | 0.00858412698412699+4.97879365079365i | 9999999999+9999999i | 0.00858412798412699+4.97879365079365i | 36053348.3035429+49788022344.229i | 9999999999.00858+10000003.9787937i | 0.00858413046294725+4.97879365078263i | 0.00868413046294725+1.8470673234701i | 5.8 | 1.8471
CAPACITOR PARAMETERS | [33 empty] | 6 | 0.0001-3.02733544973545i | 0.000000001-0.00000000000000001i | 0.00858412698412699+5.1504761904762i | 9999999999+9999999i | 0.00858412798412699+5.1504761904762i | 34336523.0784+51504847740.8828i | 9999999999.00858+10000004.1504762i | 0.00858413063684864+5.15047619046471i | 0.00868413063684864+2.12314074072926i | 6 | 2.1232
VCAP RATING (DELTA-CONNECTION) |  | 4.8 | kV | [30 empty] | 6.2 | 0.0001-2.92967946748592i | 0.000000001-0.00000000000000001i | 0.00858412698412699+5.32215873015873i | 9999999999+9999999i | 0.00858412798412699+5.32215873015873i | 32619697.8532572+53221673137.5364i | 9999999999.00858+10000004.3221587i | 0.008584130816645+5.32215873014676i | 0.008684130816645+2.39247926266084i | 6.2 | 2.3925
QRATED PER PHASE (DELTA-CONNECTION) |  | 423.8171 | kvar | [30 empty] | 6.4 | 0.0001-2.83812698412698i | 0.000000001-0.00000000000000001i | 0.00858412698412699+5.49384126984127i | 9999999999+9999999i | 0.00858412798412699+5.49384126984127i | 30902872.6281143+54938498534.1901i | 9999999999.00858+10000004.4938413i | 0.00858413100233638+5.49384126982882i | 0.00868413100233638+2.65571428570184i | 6.4 | 2.6557
Number of Caps Per Phase (N) |  | 1 | [5 empty] | Main Cap Capacitive Reactance (per can): | 54.3631 | Ohms/Capacitor | [23 empty] | 6.6 | 0.0001-2.75212313612314i | 0.000000001-0.00000000000000001i | 0.00858412698412699+5.66552380952381i | 9999999999+9999999i | 0.00858412798412699+5.66552380952381i | 29186047.4029715+56655323930.8438i | 9999999999.00858+10000004.6655238i | 0.00858413119392269+5.66552380951087i | 0.00868413119392269+2.91340067338773i | 6.6 | 2.9134
Capacitor Can KVAR Rating (kvar) |  | 423.8171 | kvar |  |  |  |  | Main Cap Capacitance (per can): | 48.7953 | µF (micro-farads)/Capacitor | [23 empty] | 6.8 | 0.0001-2.67117833800187i | 0.000000001-0.00000000000000001i | 0.00858412698412699+5.83720634920635i | 9999999999+9999999i | 0.00858412798412699+5.83720634920635i | 27469222.1778286+58372149327.4976i | 9999999999.00858+10000004.8372063i | 0.00858413139140397+5.83720634919293i | 0.00868413139140397+3.16602801119106i | 6.8 | 3.166
ICAP (Fundamental Amps Each Capacitor) |  | 80.2301 | amps | [30 empty] | 7 | 0.0001-2.5948589569161i | 0.000000001-0.00000000000000001i | 0.00858412698412699+6.00888888888889i | 9999999999+9999999i | 0.00858412798412699+6.00888888888889i | 25752396.9526858+60088974724.1513i | 9999999999.00858+10000005.0088889i | 0.00858413159478028+6.00888888887497i | 0.00868413159478028+3.41402993195887i | 7 | 3.414
IFUSE (Minimum Recommended Fuse Rating on each Capacitors) |  | 144.4142 | amps | [30 empty] | 7.2 | 0.0001-2.52277954144621i | 0.000000001-0.00000000000000001i | 0.00858412698412699+6.18057142857143i | 9999999999+9999999i | 0.00858412798412699+6.18057142857143i | 24035571.7275429+61805800120.805i | 9999999999.00858+10000005.1805714i | 0.0085841318040515+6.180571428557i | 0.0086841318040515+3.65779188711079i | 7.2 | 3.6578
VCAP FUNDAMENTAL VOLTAGE |  | 4.3719 | kV | [30 empty] | 7.4 | 0.0001-2.45459631059631i | 0.000000001-0.00000000000000001i | 0.00858412698412699+6.35225396825397i | 9999999999+9999999i | 0.00858412798412699+6.35225396825397i | 22318746.5024+63522625517.4587i | 9999999999.00858+10000005.352254i | 0.00858413201921775+6.35225396823903i | 0.00868413201921775+3.89765765764272i | 7.4 | 3.8977
VCAP RMS VOLTAGE |  | 4.3774 | kV | [30 empty] | 7.6 | 0.0001-2.39000167084378i | 0.000000001-0.00000000000000001i | 0.00858412698412699+6.52393650793651i | 9999999999+9999999i | 0.00858412798412699+6.52393650793651i | 20601921.2772572+65239450914.1124i | 9999999999.00858+10000005.5239365i | 0.00858413224027892+6.52393650792105i | 0.00868413224027892+4.13393483707727i | 7.6 | 4.1339
VPEAK CAP VOLTAGE |  | 6.491 | kV | [30 empty] | 7.8 | 0.0001-2.32871957671958i | 0.000000001-0.00000000000000001i | 0.00858412698412699+6.69561904761905i | 9999999999+9999999i | 0.00858412798412699+6.69561904761905i | 18885096.0521143+66956276310.7661i | 9999999999.00858+10000005.695619i | 0.00858413246723506+6.69561904760307i | 0.00868413246723506+4.36689947088349i | 7.8 | 4.3669
ICAP RMS CURRENT |  | 82.6993 | amps | [30 empty] | 8 | 0.0001-2.27050158730159i | 0.000000001-0.00000000000000001i | 0.00858412698412699+6.86730158730159i | 9999999999+9999999i | 0.00858412798412699+6.86730158730159i | 17168270.8269715+68673101707.4199i | 9999999999.00858+10000005.8673016i | 0.00858413270008625+6.86730158728509i | 0.00868413270008625+4.5967999999835i | 8 | 4.5968
QCAPACITOR (1-phase) |  | 355.0814 | kvar | [30 empty] | 8.2 | 0.0001-2.21512349980643i | 0.000000001-0.00000000000000001i | 0.00858412698412699+7.03898412698413i | 9999999999+9999999i | 0.00858412798412699+7.03898412698413i | 15451445.6018286+70389927104.0736i | 9999999999.00858+10000006.0389841i | 0.00858413293883233+7.0389841269671i | 0.00868413293883233+4.82386062716067i | 8.2 | 4.8239
[34 empty] | 8.4 | 0.0001-2.16238246409675i | 0.000000001-0.00000000000000001i | 0.00858412698412699+7.21066666666667i | 9999999999+9999999i | 0.00858412798412699+7.21066666666667i | 13734620.3766857+72106752500.7273i | 9999999999.00858+10000006.2106667i | 0.00858413318347345+7.21066666664909i | 0.00868413318347345+5.04828420255234i | 8.4 | 5.0483
CAPACITOR DESIGN RATINGS VS IEEE/ANSI MAXIMUMS | [33 empty] | 8.6 | 0.0001-2.11209449981543i | 0.000000001-0.00000000000000001i | 0.00858412698412699+7.38234920634921i | 9999999999+9999999i | 0.00858412798412699+7.38234920634921i | 12017795.1515429+73823577897.381i | 9999999999.00858+10000006.3823492i | 0.00858413343400948+7.38234920633109i | 0.00868413343400948+5.27025470651566i | 8.6 | 5.2703
Capacitor Duty Rating: |  | HD- Heavy Duty Capacitors, with -40C to +55C Temperature Rating | [31 empty] | 8.8 | 0.0001-2.06409235209235i | 0.000000001-0.00000000000000001i | 0.00858412698412699+7.55403174603175i | 9999999999+9999999i | 0.00858412798412699+7.55403174603175i | 10300969.9264+75540403294.0347i | 9999999999.00858+10000006.5540317i | 0.00858413369044048+7.55403174601307i | 0.00868413369044048+5.48993939392072i | 8.8 | 5.4899
|  | Capacitor Design Values |  |  |  |  | Capacitor Design Values
|  | At Nominal Voltage | At 110% System Voltage | Capacitor Rating |  |  | At Nominal Voltage | At 110% System Voltage |  | Capacitor Rating | [22 empty] | 4.8 | 9 | 0.0001-2.01822363315697i | 0.000000001-0.00000000000000001i | 0.00858412698412699+7.72571428571429i | 9999999999+9999999i | 0.00858412798412699+7.72571428571429i | 8584144.70125715+77257228690.6884i | 9999999999.00858+10000006.7257143i | 0.00858413395276652+7.72571428569506i | 0.00868413395276652+5.70749065253809i | 9 | 5.7075
% RATED VOLTS |  | 91.2% | 100.3% | 125% |  | % 60HZ AMPS: | 93.66% | 102.5% |  | 135% | [22 empty] | 6.7872 | 9.2 | 0.0001-1.97434920634921i | 0.000000001-0.00000000000000001i | 0.00858412698412699+7.89739682539683i | 9999999999+9999999i | 0.00858412798412699+7.89739682539683i | 6867319.4761143+78974054087.3421i | 9999999999.00858+10000006.8973968i | 0.00858413422098747+7.89739682537703i | 0.00868413422098747+5.92304761902782i | 9.2 | 5.9231
% CREST VOLTAGE |  | 95.64% | 105.6% | 135% |  | % 60HZ KVAR: | 83.78% | 101.2% |  | 135% | [22 empty] | 88.2952 | 9.4 | 0.0001-1.93234177642688i | 0.000000001-0.00000000000000001i | 0.00858412698412699+8.06907936507937i | 9999999999+9999999i | 0.00858412798412699+8.06907936507937i | 5150494.25097144+80690879483.9959i | 9999999999.00858+10000007.0690794i | 0.00858413449510347+8.06907936505901i | 0.00868413449510347+6.13673758863213i | 9.4 | 6.1367
[33 empty] | 423.8171 | 9.6 | 0.0001-1.89208465608466i | 0.000000001-0.00000000000000001i | 0.00858412698412699+8.24076190476191i | 9999999999+9999999i | 0.00858412798412699+8.24076190476191i | 3433669.02582857+82407704880.6496i | 9999999999.00858+10000007.2407619i | 0.00858413477511436+8.24076190474098i | 0.00868413477511436+6.34867724865632i | 9.6 | 6.3487
[34 empty] | 9.8 | 0.0001-1.8534706835115i | 0.000000001-0.00000000000000001i | 0.00858412698412699+8.41244444444444i | 9999999999+9999999i | 0.00858412798412699+8.41244444444444i | 1716843.80068582+84124530277.3032i | 9999999999.00858+10000007.4124444i | 0.00858413506102023+8.41244444442292i | 0.00868413506102023+6.55897376091142i | 9.8 | 6.559
[34 empty] | 10 | 0.0001-1.81640126984127i | 0.000000001-0.00000000000000001i | 0.00858412698412699+8.58412698412698i | 9999999999+9999999i | 0.00858412798412699+8.58412698412698i | 18.5755429565907+85841355673.9569i | 9999999999.00858+10000007.584127i | 0.00858413535282114+8.58412698410488i | 0.00868413535282114+6.76772571426361i | 10 | 6.7677
[34 empty] | 10.2 | 0.0001-1.78078555866791i | 0.000000001-0.00000000000000001i | 0.00858412698412699+8.75580952380952i | 9999999999+9999999i | 0.00858412798412699+8.75580952380952i | -1716806.64959991+87558181070.6106i | 9999999999.00858+10000007.7558095i | 0.00858413565051695+8.75580952378682i | 0.00868413565051695+6.97502396511891i | 10.2 | 6.975
[34 empty] | 10.4 | 0.0001-1.74653968253968i | 0.000000001-0.00000000000000001i | 0.00858412698412699+8.92749206349206i | 9999999999+9999999i | 0.00858412798412699+8.92749206349206i | -3433631.87474278+89275006467.2644i | 9999999999.00858+10000007.9274921i | 0.00858413595410782+8.92749206346877i | 0.00868413595410782+7.18095238092909i | 10.4 | 7.181
[34 empty] | 10.6 | 0.0001-1.71358610362384i | 0.000000001-0.00000000000000001i | 0.00858412698412699+9.0991746031746i | 9999999999+9999999i | 0.00858412798412699+9.0991746031746i | -5150457.09988563+90991831863.9181i | 9999999999.00858+10000008.0991746i | 0.00858413626359357+9.09917460315071i | 0.00868413626359357+7.38558849952687i | 10.6 | 7.3856
[34 empty] | 10.8 | 0.0001-1.68185302763081i | 0.000000001-0.00000000000000001i | 0.00858412698412699+9.27085714285714i | 9999999999+9999999i | 0.00858412798412699+9.27085714285714i | -6867282.32502849+92708657260.5718i | 9999999999.00858+10000008.2708571i | 0.00858413657897429+9.27085714283263i | 0.00868413657897429+7.58900411520182i | 10.8 | 7.589
[34 empty] | 11 | 0.0001-1.65127388167388i | 0.000000001-0.00000000000000001i | 0.00858412698412699+9.44253968253968i | 9999999999+9999999i | 0.00858412798412699+9.44253968253968i | -8584107.55017135+94425482657.2255i | 9999999999.00858+10000008.4425397i | 0.00858413690025008+9.44253968251456i | 0.00868413690025008+7.79126580084068i | 11 | 7.7913
[34 empty] | 11.2 | 0.0001-1.62178684807256i | 0.000000001-0.00000000000000001i | 0.00858412698412699+9.61422222222222i | 9999999999+9999999i | 0.00858412798412699+9.61422222222222i | -10300932.7753142+96142308053.8792i | 9999999999.00858+10000008.6142222i | 0.00858413722742075+9.61422222219647i | 0.00868413722742075+7.99243537412391i | 11.2 | 7.9924
[34 empty] | 11.4 | 0.0001-1.59333444722919i | 0.000000001-0.00000000000000001i | 0.00858412698412699+9.78590476190476i | 9999999999+9999999i | 0.00858412798412699+9.78590476190476i | -12017758.0004571+97859133450.533i | 9999999999.00858+10000008.7859048i | 0.00858413756048649+9.78590476187839i | 0.00868413756048649+8.1925703146492i | 11.4 | 8.1926
[34 empty] | 11.6 | 0.0001-1.56586316365627i | 0.000000001-0.00000000000000001i | 0.00858412698412699+9.9575873015873i | 9999999999+9999999i | 0.00858412798412699+9.9575873015873i | -13734583.2255999+99575958847.1867i | 9999999999.00858+10000008.9575873i | 0.00858413789944711+9.9575873015603i | 0.00868413789944711+8.39172413790403i | 11.6 | 8.3917
[34 empty] | 11.8 | 0.0001-1.53932311003498i | 0.000000001-0.00000000000000001i | 0.00858412698412699+10.1292698412698i | 9999999999+9999999i | 0.00858412798412699+10.1292698412698i | -15451408.4507424+101292784243.84i | 9999999999.00858+10000009.1292698i | 0.00858413824430269+10.1292698412422i | 0.00868413824430269+8.58994673120722i | 11.8 | 8.59
[34 empty] | 12 | 0.0001-1.51366772486773i | 0.000000001-0.00000000000000001i | 0.00858412698412699+10.3009523809524i | 9999999999+9999999i | 0.00858412798412699+10.3009523809524i | -17168233.6758859+103009609640.494i | 9999999999.00858+10000009.3009524i | 0.00858413859505332+10.3009523809241i | 0.00868413859505332+8.78728465605637i | 12 | 8.7873
[34 empty] | 12.2 | 0.0001-1.4888534998699i | 0.000000001-0.00000000000000001i | 0.00858412698412699+10.4726349206349i | 9999999999+9999999i | 0.00858412798412699+10.4726349206349i | -18885058.9010283+104726435037.148i | 9999999999.00858+10000009.4726349i | 0.00858413895169892+10.472634920606i | 0.00868413895169892+8.9837814207361i | 12.2 | 8.9838
Northeast Power Systems, Inc. | [33 empty] | 12.4 | 0.0001-1.46483973374296i | 0.000000001-0.00000000000000001i | 0.00858412698412699+10.6443174603175i | 9999999999+9999999i | 0.00858412798412699+10.6443174603175i | -20601884.1261718+106443260433.802i | 9999999999.00858+10000009.6443175i | 0.00858413931423949+10.6443174602879i | 0.00868413931423949+9.17947772654494i | 12.4 | 9.1795
Notch Filter Design - Stage/Branch: Branch/Stage #, Tuning Point: 4.60, Reference: Enter Job Name | [9 empty] | Page 2 | [23 empty] | 12.6 | 0.0001-1.44158830939783i | 0.000000001-0.00000000000000001i | 0.00858412698412699+10.816i | 9999999999+9999999i | 0.00858412798412699+10.816i | -22318709.3513142+108160085830.455i | 9999999999.00858+10000009.816i | 0.00858413968267494+10.8159999999697i | 0.00868413968267494+9.37441169057187i | 12.6 | 9.3744
[34 empty] | 12.8 | 0.0001-1.41906349206349i | 0.000000001-0.00000000000000001i | 0.00858412698412699+10.9876825396825i | 9999999999+9999999i | 0.00858412798412699+10.9876825396825i | -24035534.5764567+109876911227.109i | 9999999999.00858+10000009.9876825i | 0.00858414005700545+10.9876825396516i | 0.00868414005700545+9.56861904758811i | 12.8 | 9.5686
[34 empty] | 13 | 0.0001-1.39723174603175i | 0.000000001-0.00000000000000001i | 0.00858412698412699+11.1593650793651i | 9999999999+9999999i | 0.00858412798412699+11.1593650793651i | -25752359.8016002+111593736623.763i | 9999999999.00858+10000010.1593651i | 0.00858414043723095+11.1593650793335i | 0.00868414043723095+9.76213333330175i | 13 | 9.7621
[34 empty] | 13.2 | 0.0001-1.37606156806157i | 0.000000001-0.00000000000000001i | 0.00858412698412699+11.3310476190476i | 9999999999+9999999i | 0.00858412798412699+11.3310476190476i | -27469185.0267426+113310562020.416i | 9999999999.00858+10000010.3310476i | 0.00858414082335131+11.3310476190153i | 0.00868414082335131+9.95498605095373i | 13.2 | 9.955
[34 empty] | 13.4 | 0.0001-1.35552333570244i | 0.000000001-0.00000000000000001i | 0.00858412698412699+11.5027301587302i | 9999999999+9999999i | 0.00858412798412699+11.5027301587302i | -29186010.2518861+115027387417.071i | 9999999999.00858+10000010.5027302i | 0.00858414121536686+11.5027301586973i | 0.00868414121536686+10.1472068229949i | 13.4 | 10.1472
[34 empty] | 13.6 | 0.0001-1.33558916900094i | 0.000000001-0.00000000000000001i | 0.00858412698412699+11.6744126984127i | 9999999999+9999999i | 0.00858412798412699+11.6744126984127i | -30902835.4770285+116744212813.724i | 9999999999.00858+10000010.6744127i | 0.00858414161327717+11.6744126983791i | 0.00868414161327717+10.3388235293782i | 13.6 | 10.3388
[34 empty] | 13.8 | 0.0001-1.31623280423281i | 0.000000001-0.00000000000000001i | 0.00858412698412699+11.8460952380952i | 9999999999+9999999i | 0.00858412798412699+11.8460952380952i | -32619660.702171+118461038210.377i | 9999999999.00858+10000010.8460952i | 0.00858414201708244+11.8460952380608i | 0.00868414201708244+10.529862433828i | 13.8 | 10.5299
[34 empty] | 14 | 0.0001-1.29742947845805i | 0.000000001-0.00000000000000001i | 0.00858412698412699+12.0177777777778i | 9999999999+9999999i | 0.00858412798412699+12.0177777777778i | -34336485.9273145+120177863607.031i | 9999999999.00858+10000011.0177778i | 0.0085841424267828+12.0177777777427i | 0.0086841424267828+10.7203482992846i | 14 | 10.7204
[34 empty] | 14.2 | 0.0001-1.27915582383188i | 0.000000001-0.00000000000000001i | 0.00858412698412699+12.1894603174603i | 9999999999+9999999i | 0.00858412798412699+12.1894603174603i | -36053311.1524569+121894689003.685i | 9999999999.00858+10000011.1894603i | 0.00858414284237813+12.1894603174245i | 0.00868414284237813+10.9103044935926i | 14.2 | 10.9103
Harmonic #: (n) |  | 1 | 2 | 3 | 4 | 5 | 7 | 11 | 13 | [24 empty] | 14.4 | 0.0001-1.26138977072311i | 0.000000001-0.00000000000000001i | 0.00858412698412699+12.3611428571428i | 9999999999+9999999i | 0.00858412798412699+12.3611428571428i | -37770136.3775994+123611514400.338i | 9999999999.00858+10000011.3611429i | 0.00858414326386844+12.3611428571063i | 0.00868414326386844+11.0997530863832i | 14.4 | 11.0998
Filter Current (amps) (In) |  | 138.9506 | 0 | 0 | 0 | 34.7377 | 0 | 0 | 0 | [24 empty] | 14.6 | 0.0001-1.24411045879539i | 0.000000001-0.00000000000000001i | 0.00858412698412699+12.5328253968254i | 9999999999+9999999i | 0.00858412798412699+12.5328253968254i | -39486961.6027428+125328339796.992i | 9999999999.00858+10000011.5328254i | 0.00858414369125361+12.5328253967881i | 0.00868414369125361+11.2887149379927i | 14.6 | 11.2887
VCAP HARMONIC VOLTAGE (volts) |  | 4371.9018 | 0 | 0 | 0 | 218.5951 | 0 | 0 | 0 | [24 empty] | 14.8 | 0.0001-1.22729815529816i | 0.000000001-0.00000000000000001i | 0.00858412698412699+12.7045079365079i | 9999999999+9999999i | 0.00858412798412699+12.7045079365079i | -41203786.8278853+127045165193.646i | 9999999999.00858+10000011.7045079i | 0.00858414412453385+12.70450793647i | 0.00868414412453385+11.4772097811718i | 14.8 | 11.4772
IFILTER CURRENT (amps - Outside the Delta) |  | 138.9506 | 0 | 0 | 0 | 34.7377 | 0 | 0 | 0 | [24 empty] | 15 | 0.0001-1.21093417989418i | 0.000000001-0.00000000000000001i | 0.00858412698412699+12.8761904761905i | 9999999999+9999999i | 0.00858412798412699+12.8761904761905i | -42920612.0530287+128761990590.3i | 9999999999.00858+10000011.8761905i | 0.0085841445637091+12.8761904761518i | 0.0086841445637091+11.6652562962576i | 15 | 11.6653
IREACTOR CURRENT (AMPS INSIDE THE DELTA) |  | 80.2301 | 0 | 0 | 0 | 20.0575 | 0 | 0 | 0 | [24 empty] | 15.2 | 0.0001-1.19500083542189i | 0.000000001-0.00000000000000001i | 0.00858412698412699+13.047873015873i | 9999999999+9999999i | 0.00858412798412699+13.047873015873i | -44637437.2781712+130478815986.953i | 9999999999.00858+10000012.047873i | 0.00858414500877917+13.0478730158335i | 0.00868414500877917+11.8528721804116i | 15.2 | 11.8529
[34 empty] | 15.4 | 0.0001-1.17948134405277i | 0.000000001-0.00000000000000001i | 0.00858412698412699+13.2195555555555i | 9999999999+9999999i | 0.00858412798412699+13.2195555555555i | -46354262.5033137+132195641383.607i | 9999999999.00858+10000012.2195556i | 0.00858414545974446+13.2195555555154i | 0.00868414545974446+12.0400742114626i | 15.4 | 12.0401
Harmonic #: (n) |  | 17 | 19 | 23 | 25 | 29 | 31 | 35 | 37 | [5 empty] | 1 | 2 | 3 | 4 | 5 | 7 | 11 | 13 | [11 empty] | 15.6 | 0.0001-1.16435978835979i | 0.000000001-0.00000000000000001i | 0.00858412698412699+13.3912380952381i | 9999999999+9999999i | 0.00858412798412699+13.3912380952381i | -48071087.7284571+133912466780.261i | 9999999999.00858+10000012.3912381i | 0.00858414591660449+13.3912380951972i | 0.00868414591660449+12.2268783068374i | 15.6 | 12.2269
Filter Current (amps) (In) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | VCAP HARMONIC VOLTAGE (volts)^2 | 19113525.254 | 0 | 0 | 0 | 47783.8131 | 0 | 0 | 0 | [11 empty] | 15.8 | 0.0001-1.14962105686157i | 0.000000001-0.00000000000000001i | 0.00858412698412699+13.5629206349206i | 9999999999+9999999i | 0.00858412798412699+13.5629206349206i | -49787912.9535996+135629292176.914i | 9999999999.00858+10000012.5629206i | 0.00858414637935949+13.5629206348789i | 0.00868414637935949+12.4132995780173i | 15.8 | 12.4133
VCAP HARMONIC VOLTAGE (volts) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | Filter Current (amps) (In)^2 | 19307.2817 | 0 | 0 | 0 | 1206.7051 | 0 | 0 | 0 | [11 empty] | 16 | 0.0001-1.1352507936508i | 0.000000001-0.00000000000000001i | 0.00858412698412699+13.7346031746032i | 9999999999+9999999i | 0.00858412798412699+13.7346031746032i | -51504738.1787431+137346117573.569i | 9999999999.00858+10000012.7346032i | 0.00858414684800969+13.7346031745608i | 0.00868414684800969+12.59935238091i | 16 | 12.5994
IFILTER CURRENT (amps - Outside the Delta) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | kvar (single phase) | 350.6977 | 0 | 0 | 0 | 4.3837 | 0 | 0 | 0 | [11 empty] | 16.2 | 0.0001-1.12123535175387i | 0.000000001-0.00000000000000001i | 0.00858412698412699+13.9062857142857i | 9999999999+9999999i | 0.00858412798412699+13.9062857142857i | -53221563.4038855+139062942970.222i | 9999999999.00858+10000012.9062857i | 0.00858414732255464+13.9062857142425i | 0.00868414732255464+12.7850503624886i | 16.2 | 12.7851
IREACTOR CURRENT (AMPS INSIDE THE DELTA) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [24 empty] | 16.4 | 0.0001-1.10756174990322i | 0.000000001-0.00000000000000001i | 0.00858412698412699+14.0779682539682i | 9999999999+9999999i | 0.00858412798412699+14.0779682539682i | -54938388.629028+140779768366.875i | 9999999999.00858+10000013.0779683i | 0.00858414780299469+14.0779682539242i | 0.00868414780299469+12.970406504021i | 16.4 | 12.9704
[34 empty] | 16.6 | 0.0001-1.0942176324345i | 0.000000001-0.00000000000000001i | 0.00858412698412699+14.2496507936508i | 9999999999+9999999i | 0.00858412798412699+14.2496507936508i | -56655213.8541714+142496593763.53i | 9999999999.00858+10000013.2496508i | 0.00858414828932969+14.2496507936061i | 0.00868414828932969+13.1554331611716i | 16.6 | 13.1554
FILTER ONE-LINE DIAGRAM | [14 empty] | 17 | 19 | 23 | 25 | 29 | 31 | 35 | 37 | [11 empty] | 16.8 | 0.0001-1.08119123204838i | 0.000000001-0.00000000000000001i | 0.00858412698412699+14.4213333333333i | 9999999999+9999999i | 0.00858412798412699+14.4213333333333i | -58372039.0793139+144213419160.183i | 9999999999.00858+10000013.4213333i | 0.00858414878155955+14.4213333332878i | 0.00868414878155955+13.3401421012394i | 16.8 | 13.3401
|  | Fundamental amps 139 amps/phase | [5 empty] | Reactor Fundamental Design Margin: | 1.35 |  |  |  |  | VCAP HARMONIC VOLTAGE (volts)^2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [11 empty] | 17 | 0.0001-1.06847133520075i | 0.000000001-0.00000000000000001i | 0.00858412698412699+14.5930158730159i | 9999999999+9999999i | 0.00858412798412699+14.5930158730159i | -60088864.3044574+145930244556.837i | 9999999999.00858+10000013.5930159i | 0.00858414927968452+14.5930158729695i | 0.00868414927968452+13.5245445377688i | 17 | 13.5245
|  | RMS AMPS 143.23 amps/phase | [5 empty] | Reactor Harmonic Design Margin: | 1 |  |  |  |  | Filter Current (amps) (In)^2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [11 empty] | 17.2 | 0.0001-1.05604724990772i | 0.000000001-0.00000000000000001i | 0.00858412698412699+14.7646984126984i | 9999999999+9999999i | 0.00858412798412699+14.7646984126984i | -61805689.5295998+147647069953.491i | 9999999999.00858+10000013.7646984i | 0.00858414978370443+14.7646984126513i | 0.00868414978370443+13.7086511627436i | 17.2 | 13.7087
[14 empty] | kvar (single phase) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [11 empty] | 17.4 | 0.0001-1.04390877577085i | 0.000000001-0.00000000000000001i | 0.00858412698412699+14.9363809523809i | 9999999999+9999999i | 0.00858412798412699+14.9363809523809i | -63522514.7547423+149363895350.144i | 9999999999.00858+10000013.936381i | 0.00858415029361936+14.936380952333i | 0.00868415029361936+13.8924721765621i | 17.4 | 13.8925
[6 empty] | Reference: Notch Filter Design - Stage/Branch: Branch/Stage #, Tuning Point: 4.60, Reference: Enter Job Name | [27 empty] | 17.6 | 0.0001-1.03204617604618i | 0.000000001-0.00000000000000001i | 0.00858412698412699+15.1080634920635i | 9999999999+9999999i | 0.00858412798412699+15.1080634920635i | -65239339.9798858+151080720746.798i | 9999999999.00858+10000014.1080635i | 0.00858415080942911+15.1080634920147i | 0.00868415080942911+14.0760173159685i | 17.6 | 14.076
[34 empty] | 17.8 | 0.0001-1.02045015159622i | 0.000000001-0.00000000000000001i | 0.00858412698412699+15.279746031746i | 9999999999+9999999i | 0.00858412798412699+15.279746031746i | -66956165.2050282+152797546143.452i | 9999999999.00858+10000014.279746i | 0.00858415133113393+15.2797460316965i | 0.00868415133113393+14.2592958801003i | 17.8 | 14.2593
[6 empty] | Current Ratings |  |  | Design & Construction Details | [24 empty] | 18 | 0.0001-1.00911181657849i | 0.000000001-0.00000000000000001i | 0.00858412698412699+15.4514285714286i | 9999999999+9999999i | 0.00858412798412699+15.4514285714286i | -68672990.4301717+154514371540.106i | 9999999999.00858+10000014.4514286i | 0.00858415185873378+15.4514285713782i | 0.00868415185873378+14.4423167547997i | 18 | 14.4423
[6 empty] | Harm # | Amps |  | Quantity: | 1 | [23 empty] | 18.2 | 0.0001-0.998022675736963i | 0.000000001-0.00000000000000001i | 0.00858412698412699+15.6231111111111i | 9999999999+9999999i | 0.00858412798412699+15.6231111111111i | -70389815.6553141+156231196936.759i | 9999999999.00858+10000014.6231111i | 0.00858415239222846+15.6231111110599i | 0.00868415239222846+14.6250884353229i | 18.2 | 14.6251
[6 empty] | 1 | 108.3106 |  | Number of Phases: | 3 |  |  |  | harmonic # | 1 | 2 | 3 | 4 | 5 | 7 | 11 | 13 | 17 | 19 | 23 | 25 | 29 | 31 | 35 | 37 |  |  |  | 18.4 | 0.0001-0.987174603174605i | 0.000000001-0.00000000000000001i | 0.00858412698412699+15.7947936507936i | 9999999999+9999999i | 0.00858412798412699+15.7947936507936i | -72106640.8804566+157948022333.412i | 9999999999.00858+10000014.7947937i | 0.00858415293161825+15.7947936507415i | 0.00868415293161825+14.8076190475669i | 18.4 | 14.8076 |  | 108.3106 | 11731.1943
[6 empty] | 2 | 0 |  | System Voltage: | 4.16 kV |  |  |  | Total filter amps | 138.9506 | 0 | 0 | 0 | 34.7377 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 18.6 | 0.0001-0.976559822495308i | 0.000000001-0.00000000000000001i | 0.00858412698412699+15.9664761904762i | 9999999999+9999999i | 0.00858412798412699+15.9664761904762i | -73823466.1056+159664847730.067i | 9999999999.00858+10000014.9664762i | 0.00858415347690296+15.9664761904233i | 0.00868415347690296+14.989916367928i | 18.6 | 14.9899 |  | 0 | 0
[6 empty] | 3 | 0 |  | BIL Rating (kV): | 95 |  |  |  | R & X EQUIVALENT IMPEDANCE | 0.85841 | 1.7168 | 2.5752 | 3.4337 | 4.2921 | 6.0089 | 9.4425 | 11.1594 | 14.593 | 16.3098 | 19.7435 | 21.4603 | 24.894 | 26.6108 | 30.0444 | 31.7613 |  |  |  | 18.8 | 0.0001-0.966170888213443i | 0.000000001-0.00000000000000001i | 0.00858412698412699+16.1381587301587i | 9999999999+9999999i | 0.00858412798412699+16.1381587301587i | -75540291.3307425+161381673126.72i | 9999999999.00858+10000015.1381587i | 0.00858415402808255+16.1381587301049i | 0.00868415402808255+15.1719878418915i | 18.8 | 15.172 |  | 0 | 0
Capacitor: Qty(3), 424 kvar, 4.8 kV, 48.8 µF/Can | [5 empty] | 4 | 0 |  | Fundamental Frequency: | 60 |  |  |  | I FILTER AMPS | 138.9506 | 0 | 0 | 0 | 34.7377 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 19 | 0.0001-0.956000668337512i | 0.000000001-0.00000000000000001i | 0.00858412698412699+16.3098412698412i | 9999999999+9999999i | 0.00858412798412699+16.3098412698412i | -77257116.555885+163098498523.373i | 9999999999.00858+10000015.3098413i | 0.00858415458515726+16.3098412697866i | 0.00868415458515726+15.3538406014491i | 19 | 15.3538 |  | 0 | 0
[6 empty] | 5 | 20.0575 |  | Inductance (mH): | 6.8312 | [23 empty] | 19.2 | 0.0001-0.94604232804233i | 0.000000001-0.00000000000000001i | 0.00858412698412699+16.4815238095238i | 9999999999+9999999i | 0.00858412798412699+16.4815238095238i | -78973941.7810284+164815323920.028i | 9999999999.00858+10000015.4815238i | 0.0085841551481269+16.4815238094684i | 0.0086841551481269+15.5354814814261i | 19.2 | 15.5355 |  | 20.0575 | 402.3043
Capacitor Fuse: 144 (Minimum Amps) | [5 empty] | 7 | 0 |  | Reactance at 60Hz (ohms): | 2.5752 | [23 empty] | 19.4 | 0.0001-0.936289314351172i | 0.000000001-0.00000000000000001i | 0.00858412698412699+16.6532063492063i | 9999999999+9999999i | 0.00858412798412699+16.6532063492063i | -80690767.0061709+166532149316.681i | 9999999999.00858+10000015.6532063i | 0.00858415571699139+16.65320634915i | 0.00868415571699139+15.7169170347988i | 19.4 | 15.7169 |  | 0 | 0
[6 empty] | 11 | 0 |  | Taps: | None | [23 empty] | 19.6 | 0.0001-0.926735341755752i | 0.000000001-0.00000000000000001i | 0.00858412698412699+16.8248888888889i | 9999999999+9999999i | 0.00858412798412699+16.8248888888889i | -82407592.2313143+168248974713.335i | 9999999999.00858+10000015.8248889i | 0.00858415629175104+16.8248888888317i | 0.00868415629175104+15.8981535470759i | 19.6 | 15.8982 |  | 0 | 0
[6 empty] | 13 | 0 |  | Insulation Type: | Nomex |  |  |  | Total filter amps^2 | 19307.2817 | 0 | 0 | 0 | 1206.7051 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Total Filter RMS Amps | 143.227 |  | 19.8 | 0.0001-0.917374378707714i | 0.000000001-0.00000000000000001i | 0.00858412698412699+16.9965714285714i | 9999999999+9999999i | 0.00858412798412699+16.9965714285714i | -84124417.4564568+169965800109.989i | 9999999999.00858+10000015.9965714i | 0.00858415687240558+16.9965714285134i | 0.00868415687240558+16.0791970498057i | 19.8 | 16.0792 |  | 0 | 0
Iron-Core Filter Reactor: 2.58 ohms, 6.83 mH | [5 empty] | 17 | 0 |  | Ambient: | 60C |  |  |  | I2R REACTOR LOSSES | 497.2085 | 0 | 0 | 0 | 31.0755 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 20 | 0.0001-0.908200634920637i | 0.000000001-0.00000000000000001i | 0.00858412698412699+17.1682539682539i | 9999999999+9999999i | 0.00858412798412699+17.1682539682539i | -85841242.6815993+171682625506.642i | 9999999999.00858+10000016.168254i | 0.00858415745895517+17.168253968195i | 0.00868415745895517+16.2600533332744i | 20 | 16.2601 |  | 0 | 0
I1= 80.3 amps nominal, Irms = 82.7 amps nominal | [5 empty] | 19 | 0 |  | Temperature Rise: | 115C Rise over Ambient | [23 empty] | 20.2 | 0.0001-0.899208549426373i | 0.000000001-0.00000000000000001i | 0.00858412698412699+17.3399365079365i | 9999999999+9999999i | 0.00858412798412699+17.3399365079365i | -87558067.9067427+173399450903.296i | 9999999999.00858+10000016.3399365i | 0.00858415805139957+17.3399365078766i | 0.00868415805139957+16.4407279584502i | 20.2 | 16.4407 |  | 0 | 0
[6 empty] | 23 | 0 |  | Winding Type: | CU/AL - Based On Price | [23 empty] | 20.4 | 0.0001-0.890392779333958i | 0.000000001-0.00000000000000001i | 0.00858412698412699+17.511619047619i | 9999999999+9999999i | 0.00858412798412699+17.511619047619i | -89274893.1318852+175116276299.95i | 9999999999.00858+10000016.511619i | 0.00858415864973903+17.5116190475583i | 0.00868415864973903+16.6212262682243i | 20.4 | 16.6212 |  | 0 | 0
[6 empty] | 25 | 0 |  | Tack Winding to Core: | Yes | [23 empty] | 20.6 | 0.0001-0.881748189243337i | 0.000000001-0.00000000000000001i | 0.00858412698412699+17.6833015873016i | 9999999999+9999999i | 0.00858412798412699+17.6833015873016i | -90991718.3570286+176833101696.604i | 9999999999.00858+10000016.6833016i | 0.00858415925397354+17.68330158724i | 0.00868415925397354+16.8015533979967i | 20.6 | 16.8016 |  | 0 | 0
[6 empty] | 29 | 0 |  | Enclosure: | None/Open Construction | [23 empty] | 20.8 | 0.0001-0.873269841269843i | 0.000000001-0.00000000000000001i | 0.00858412698412699+17.8549841269841i | 9999999999+9999999i | 0.00858412798412699+17.8549841269841i | -92708543.5821711+178549927093.257i | 9999999999.00858+10000016.8549841i | 0.00858415986410285+17.8549841269215i | 0.00868415986410285+16.9817142856517i | 20.8 | 16.9817 |  | 0 | 0
[6 empty] | 31 | 0 | [26 empty] | 21 | 0.0001-0.864952985638702i | 0.000000001-0.00000000000000001i | 0.00858412698412699+18.0266666666666i | 9999999999+9999999i | 0.00858412798412699+18.0266666666666i | -94425368.8073136+180266752489.911i | 9999999999.00858+10000017.0266667i | 0.0085841604801274+18.0266666666032i | 0.0086841604801274+17.1617136809645i | 21 | 17.1617 |  | 0 | 0
4.16kV, 60Hz Notch Filter, Delta Connected | [5 empty] | 35 | 0 | [26 empty] | 21.2 | 0.0001-0.856793051811922i | 0.000000001-0.00000000000000001i | 0.00858412698412699+18.1983492063492i | 9999999999+9999999i | 0.00858412798412699+18.1983492063492i | -96142194.032457+181983577886.565i | 9999999999.00858+10000017.1983492i | 0.00858416110204666+18.1983492062849i | 0.00868416110204666+17.341556154473i | 21.2 | 17.3416 |  | 0 | 0
1000 MVAR 3-Phase, 4.6 Tuning | [5 empty] | 37 | 0 | [26 empty] | 21.4 | 0.0001-0.848785640112745i | 0.000000001-0.00000000000000001i | 0.00858412698412699+18.3700317460317i | 9999999999+9999999i | 0.00858412798412699+18.3700317460317i | -97859019.2575995+183700403283.218i | 9999999999.00858+10000017.3700317i | 0.00858416172986088+18.3700317459664i | 0.00868416172986088+17.5212461058537i | 21.4 | 17.5212 |  | 0 | 0
[6 empty] | RMS: | 110.1522 | [26 empty] | 21.6 | 0.0001-0.840926513815405i | 0.000000001-0.00000000000000001i | 0.00858412698412699+18.5417142857143i | 9999999999+9999999i | 0.00858412798412699+18.5417142857143i | -99575844.4827429+185417228679.873i | 9999999999.00858+10000017.5417143i | 0.00858416236357036+18.5417142856481i | 0.00868416236357036+17.7007877718327i | 21.6 | 17.7008 |  |  | 12133.4986
[34 empty] | 21.8 | 0.0001-0.833211591670309i | 0.000000001-0.00000000000000001i | 0.00858412698412699+18.7133968253968i | 9999999999+9999999i | 0.00858412798412699+18.7133968253968i | -101292669.707885+187134054076.526i | 9999999999.00858+10000017.7133968i | 0.00858416300317457+18.7133968253297i | 0.00868416300317457+17.8801852336594i | 21.8 | 17.8802 |  |  | 110.1522 | reactor RMS amps (for supplier with margin)
[34 empty] | 22 | 0.0001-0.825636940836943i | 0.000000001-0.00000000000000001i | 0.00858412698412699+18.8850793650793i | 9999999999+9999999i | 0.00858412798412699+18.8850793650793i | -103009494.933028+188850879473.179i | 9999999999.00858+10000017.8850794i | 0.00858416364867385+18.8850793650112i | 0.00868416364867385+18.0594424241743i | 22 | 18.0594
Where: | [33 empty] | 22.2 | 0.0001-0.818198770198772i | 0.000000001-0.00000000000000001i | 0.00858412698412699+19.0567619047619i | 9999999999+9999999i | 0.00858412798412699+19.0567619047619i | -104726320.158171+190567704869.833i | 9999999999.00858+10000018.0567619i | 0.00858416430006801+19.0567619046928i | 0.00868416430006801+18.238563134494i | 22.2 | 18.2386
Xeff | Effective reactance of the harmonic filter | [32 empty] | 22.4 | 0.0001-0.810893424036283i | 0.000000001-0.00000000000000001i | 0.00858412698412699+19.2284444444444i | 9999999999+9999999i | 0.00858412798412699+19.2284444444444i | -106443145.383314+192284530266.487i | 9999999999.00858+10000018.2284444i | 0.00858416495735714+19.2284444443744i | 0.00868416495735714+18.4175510203381i | 22.4 | 18.4176
Qeff | Effective Reactive Power (MVAR) of the harmonic filter (fundamental current only, not including harmonics) | [32 empty] | 22.6 | 0.0001-0.803717376035962i | 0.000000001-0.00000000000000001i | 0.00858412698412699+19.4001269841269i | 9999999999+9999999i | 0.00858412798412699+19.4001269841269i | -108159970.608456+194001355663.14i | 9999999999.00858+10000018.400127i | 0.00858416562054144+19.400126984056i | 0.00868416562054144+18.59640960802i | 22.6 | 18.5964
QFILTER | Kvar rating of harmonic filter. Includes reactive power associated with fundamental and harmonic current. | [32 empty] | 22.8 | 0.0001-0.796667223614594i | 0.000000001-0.00000000000000001i | 0.00858412698412699+19.5718095238095i | 9999999999+9999999i | 0.00858412798412699+19.5718095238095i | -109876795.8336+195718181059.794i | 9999999999.00858+10000018.5718095i | 0.00858416628962042+19.5718095237376i | 0.00868416628962042+18.775142300123i | 22.8 | 18.7751
QRATED PER PHASE | kvar rating of capacitors at their rated voltage (not the application voltage) | [32 empty] | 23 | 0.0001-0.789739682539684i | 0.000000001-0.00000000000000001i | 0.00858412698412699+19.743492063492i | 9999999999+9999999i | 0.00858412798412699+19.743492063492i | -111593621.058742+197435006456.448i | 9999999999.00858+10000018.7434921i | 0.00858416696459476+19.7434920634192i | 0.00868416696459476+18.9537523808795i | 23 | 18.9538
VLLSYS | Nominal System Line-to-Line Voltage | [32 empty] | 23.2 | 0.0001-0.782931581828135i | 0.000000001-0.00000000000000001i | 0.00858412698412699+19.9151746031746i | 9999999999+9999999i | 0.00858412798412699+19.9151746031746i | -113310446.283886+199151831853.102i | 9999999999.00858+10000018.9151746i | 0.00858416764546368+19.9151746031007i | 0.00868416764546368+19.1322430212726i | 23.2 | 19.1322
XC | Capacitive reactance of the harmonic filter capacitor at fundamental frequency | [32 empty] | 23.4 | 0.0001-0.776239858906527i | 0.000000001-0.00000000000000001i | 0.00858412698412699+20.0868571428571i | 9999999999+9999999i | 0.00858412798412699+20.0868571428571i | -115027271.509028+200868657249.755i | 9999999999.00858+10000019.0868571i | 0.00858416833222767+20.0868571427822i | 0.00868416833222767+19.3106172838757i | 23.4 | 19.3106
XL | Inductive Reactance of the harmonic filter reactor at fundamental frequency | [32 empty] | 23.6 | 0.0001-0.769661555017489i | 0.000000001-0.00000000000000001i | 0.00858412698412699+20.2585396825396i | 9999999999+9999999i | 0.00858412798412699+20.2585396825396i | -116744096.734171+202585482646.409i | 9999999999.00858+10000019.2585397i | 0.00858416902488684+20.2585396824638i | 0.00868416902488684+19.4888781274463i | 23.6 | 19.4889
h | harmonic number of tuning filter tuning point | [32 empty] | 23.8 | 0.0001-0.763193810857678i | 0.000000001-0.00000000000000001i | 0.00858412698412699+20.4302222222222i | 9999999999+9999999i | 0.00858412798412699+20.4302222222222i | -118460921.959314+204302308043.063i | 9999999999.00858+10000019.4302222i | 0.00858416972344078+20.4302222221454i | 0.00868416972344078+19.6670284112877i | 23.8 | 19.667
f | frequency | [32 empty] | 24 | 0.0001-0.756833862433864i | 0.000000001-0.00000000000000001i | 0.00858412698412699+20.6019047619047i | 9999999999+9999999i | 0.00858412798412699+20.6019047619047i | -120177747.184456+206019133439.716i | 9999999999.00858+10000019.6019048i | 0.0085841704278899+20.6019047618269i | 0.0086841704278899+19.845070899393i | 24 | 19.8451
H | Reactor Henry Rating (milliHenrys) | [32 empty] | 24.2 | 0.0001-0.750579037124493i | 0.000000001-0.00000000000000001i | 0.00858412698412699+20.7735873015873i | 9999999999+9999999i | 0.00858412798412699+20.7735873015873i | -121894572.4096+207735958836.371i | 9999999999.00858+10000019.7735873i | 0.00858417113823378+20.7735873015085i | 0.00868417113823378+20.023008264384i | 24.2 | 20.023
IRATED FUNDAMENTAL | Fundamental Current Rating of Filter Bank | [32 empty] | 24.4 | 0.0001-0.744426749934949i | 0.000000001-0.00000000000000001i | 0.00858412698412699+20.9452698412698i | 9999999999+9999999i | 0.00858412798412699+20.9452698412698i | -123611397.634742+209452784233.024i | 9999999999.00858+10000019.9452698i | 0.00858417185447263+20.94526984119i | 0.00868417185447263+20.2008430912551i | 24.4 | 20.2008
VCAP FUNDAMENTAL VOLTAGE | Fundamental Voltage Drop Across Capacitor | [32 empty] | 24.6 | 0.0001-0.738374499935477i | 0.000000001-0.00000000000000001i | 0.00858412698412699+21.1169523809523i | 9999999999+9999999i | 0.00858412798412699+21.1169523809523i | -125328222.859885+211169609629.677i | 9999999999.00858+10000020.1169524i | 0.00858417257660657+21.1169523808714i | 0.00868417257660657+20.3785778809359i | 24.6 | 20.3786
VCAP HARMONIC VOLTAGE | Harmonic Voltage Drop Across Capacitor | [32 empty] | 24.8 | 0.0001-0.732419866871482i | 0.000000001-0.00000000000000001i | 0.00858412698412699+21.2886349206349i | 9999999999+9999999i | 0.00858412798412699+21.2886349206349i | -127045048.085028+212886435026.332i | 9999999999.00858+10000020.2886349i | 0.00858417330463547+21.2886349205531i | 0.00868417330463547+20.5562150536816i | 24.8 | 20.5562
VCAP RMS VOLTAGE | Capacitor RMS Voltage (Fundamental Voltage + Harmonic Voltages) | [32 empty] | 25 | 0.0001-0.72656050793651i | 0.000000001-0.00000000000000001i | 0.00858412698412699+21.4603174603174i | 9999999999+9999999i | 0.00858412798412699+21.4603174603174i | -128761873.310171+214603260422.985i | 9999999999.00858+10000020.4603175i | 0.00858417403855936+21.4603174602345i | 0.00868417403855936+20.733756952298i | 25 | 20.7338
VPEAK CAP VOLTAGE | Capacitor Voltage assuming or harmonics are coincident | [32 empty] | 25.2 | 0.0001-0.720794154698918i | 0.000000001-0.00000000000000001i | 0.00858412698412699+21.632i | 9999999999+9999999i | 0.00858412798412699+21.632i | -130478698.535314+216320085819.639i | 9999999999.00858+10000020.632i | 0.0085841747783781+21.6319999999161i | 0.0086841747783781+20.9112058452172i | 25.2 | 20.9112
N | Number of Capacitors per phase | [32 empty] | 25.4 | 0.0001-0.71511861017373i | 0.000000001-0.00000000000000001i | 0.00858412698412699+21.8036825396825i | 9999999999+9999999i | 0.00858412798412699+21.8036825396825i | -132195523.760457+218036911216.293i | 9999999999.00858+10000020.8036825i | 0.00858417552409182+21.8036825395976i | 0.00868417552409182+21.0885639294239i | 25.4 | 21.0886
VCAP var rating | Capacitor Can Var Rating (in Kvar) | [32 empty] | 25.6 | 0.0001-0.709531746031748i | 0.000000001-0.00000000000000001i | 0.00858412698412699+21.975365079365i | 9999999999+9999999i | 0.00858412798412699+21.975365079365i | -133912348.985599+219753736612.946i | 9999999999.00858+10000020.9753651i | 0.00858417627570073+21.975365079279i | 0.00868417627570073+21.2658333332473i | 25.6 | 21.2658
ICAP RMS CURRENT | RMS Current Seen By Capacitor (amps) | [32 empty] | 25.8 | 0.0001-0.704031499938478i | 0.000000001-0.00000000000000001i | 0.00858412698412699+22.1470476190476i | 9999999999+9999999i | 0.00858412798412699+22.1470476190476i | -135629174.210743+221470562009.6i | 9999999999.00858+10000021.1470476i | 0.00858417703320429+22.1470476189605i | 0.00868417703320429+21.443016119022i | 25.8 | 21.443
IFILTER RMS CURRENT | RMS Current into Filter Branch (amps) | [32 empty] | 26 | 0.0001-0.698615873015875i | 0.000000001-0.00000000000000001i | 0.00858412698412699+22.3187301587301i | 9999999999+9999999i | 0.00858412798412699+22.3187301587301i | -137345999.435885+223187387406.254i | 9999999999.00858+10000021.3187302i | 0.00858417779660325+22.318730158642i | 0.00868417779660325+21.6201142856261i | 26 | 21.6201
DF | Damping Factor is defined as the resistance of the resistor to the reactance of the reactor at the filter tuned frequency | [32 empty] | 26.2 | 0.0001-0.693282927420334i | 0.000000001-0.00000000000000001i | 0.00858412698412699+22.4904126984127i | 9999999999+9999999i | 0.00858412798412699+22.4904126984127i | -139062824.661029+224904212802.908i | 9999999999.00858+10000021.4904127i | 0.00858417856589675+22.4904126983235i | 0.00868417856589675+21.7971297709032i | 26.2 | 21.7971
* Formulas taken From IEEE Std. 1531-2003 - IEEE Guide for Application and Specification of Harmonic Filters | [33 empty] | 26.4 | 0.0001-0.688030784030786i | 0.000000001-0.00000000000000001i | 0.00858412698412699+22.6620952380952i | 9999999999+9999999i | 0.00858412798412699+22.6620952380952i | -140779649.886171+226621038199.561i | 9999999999.00858+10000021.6620952i | 0.00858417934108533+22.6620952380049i | 0.00868417934108533+21.9740644539741i | 26.4 | 21.9741
[34 empty] | 26.6 | 0.0001-0.682857620241081i | 0.000000001-0.00000000000000001i | 0.00858412698412699+22.8337777777777i | 9999999999+9999999i | 0.00858412798412699+22.8337777777777i | -142496475.111313+228337863596.215i | 9999999999.00858+10000021.8337778i | 0.00858418012216921+22.8337777776864i | 0.00868418012216921+22.1509201574453i | 26.6 | 22.1509
[34 empty] | 26.8 | 0.0001-0.677761667851222i | 0.000000001-0.00000000000000001i | 0.00858412698412699+23.0054603174603i | 9999999999+9999999i | 0.00858412798412699+23.0054603174603i | -144213300.336457+230054688992.869i | 9999999999.00858+10000022.0054603i | 0.00858418090914763+23.0054603173679i | 0.00868418090914763+22.3276986495167i | 26.8 | 22.3277
[34 empty] | 27 | 0.0001-0.672741211052324i | 0.000000001-0.00000000000000001i | 0.00858412698412699+23.1771428571428i | 9999999999+9999999i | 0.00858412798412699+23.1771428571428i | -145930125.561599+231771514389.522i | 9999999999.00858+10000022.1771429i | 0.00858418170202136+23.1771428570493i | 0.00868418170202136+22.504401645997i | 27 | 22.5044
[34 empty] | 27.2 | 0.0001-0.667794584500469i | 0.000000001-0.00000000000000001i | 0.00858412698412699+23.3488253968254i | 9999999999+9999999i | 0.00858412798412699+23.3488253968254i | -147646950.786743+233488339786.176i | 9999999999.00858+10000022.3488254i | 0.00858418250078973+23.3488253967308i | 0.00868418250078973+22.6810308122303i | 27.2 | 22.681
[34 empty] | 27.4 | 0.0001-0.662920171474918i | 0.000000001-0.00000000000000001i | 0.00858412698412699+23.5205079365079i | 9999999999+9999999i | 0.00858412798412699+23.5205079365079i | -149363776.011885+235205165182.83i | 9999999999.00858+10000022.5205079i | 0.00858418330545327+23.5205079364122i | 0.00868418330545327+22.8575877649373i | 27.4 | 22.8576
Northeast Power Systems, Inc. | [33 empty] | 27.6 | 0.0001-0.658116402116404i | 0.000000001-0.00000000000000001i | 0.00858412698412699+23.6921904761904i | 9999999999+9999999i | 0.00858412798412699+23.6921904761904i | -151080601.237028+236921990579.483i | 9999999999.00858+10000022.6921905i | 0.00858418411601182+23.6921904760936i | 0.00868418411601182+23.0340740739772i | 27.6 | 23.0341
Notch Filter Design - Stage/Branch: Branch/Stage #, Tuning Point: 4.60, Reference: Enter Job Name | [9 empty] | Page 3 | [23 empty] | 27.8 | 0.0001-0.653381751741466i | 0.000000001-0.00000000000000001i | 0.00858412698412699+23.863873015873i | 9999999999+9999999i | 0.00858412798412699+23.863873015873i | -152797426.462171+238638815976.137i | 9999999999.00858+10000022.863873i | 0.0085841849324652+23.8638730157751i | 0.0086841849324652+23.2104912640336i | 27.8 | 23.2105
[34 empty] | 28 | 0.0001-0.648714739229027i | 0.000000001-0.00000000000000001i | 0.00858412698412699+24.0355555555555i | 9999999999+9999999i | 0.00858412798412699+24.0355555555555i | -154514251.687314+240355641372.791i | 9999999999.00858+10000023.0355556i | 0.00858418575481379+24.0355555554565i | 0.00868418575481379+23.3868408162275i | 28 | 23.3868
[34 empty] | 28.2 | 0.0001-0.644113925475629i | 0.000000001-0.00000000000000001i | 0.00858412698412699+24.207238095238i | 9999999999+9999999i | 0.00858412798412699+24.207238095238i | -156231076.912456+242072466769.444i | 9999999999.00858+10000023.2072381i | 0.00858418658305713+24.2072380951378i | 0.00868418658305713+23.5631241696622i | 28.2 | 23.5631
[34 empty] | 28.4 | 0.0001-0.639577911915942i | 0.000000001-0.00000000000000001i | 0.00858412698412699+24.3789206349206i | 9999999999+9999999i | 0.00858412798412699+24.3789206349206i | -157947902.1376+243789292166.098i | 9999999999.00858+10000023.3789206i | 0.00858418741719533+24.3789206348193i | 0.00868418741719533+23.7393427229034i | 28.4 | 23.7393
[34 empty] | 28.6 | 0.0001-0.635105339105341i | 0.000000001-0.00000000000000001i | 0.00858412698412699+24.5506031746031i | 9999999999+9999999i | 0.00858412798412699+24.5506031746031i | -159664727.362742+245506117562.752i | 9999999999.00858+10000023.5506032i | 0.00858418825722895+24.5506031745007i | 0.00868418825722895+23.9154978353954i | 28.6 | 23.9155
[34 empty] | 28.8 | 0.0001-0.630694885361554i | 0.000000001-0.00000000000000001i | 0.00858412698412699+24.7222857142857i | 9999999999+9999999i | 0.00858412798412699+24.7222857142857i | -161381552.587886+247222942959.406i | 9999999999.00858+10000023.7222857i | 0.00858418910315709+24.7222857141822i | 0.00868418910315709+24.0915908288206i | 28.8 | 24.0916
[34 empty] | 29 | 0.0001-0.626345265462508i | 0.000000001-0.00000000000000001i | 0.00858412698412699+24.8939682539682i | 9999999999+9999999i | 0.00858412798412699+24.8939682539682i | -163098377.813028+248939768356.059i | 9999999999.00858+10000023.8939683i | 0.00858418995498056+24.8939682538635i | 0.00868418995498056+24.267622988401i | 29 | 24.2676
[34 empty] | 29.2 | 0.0001-0.622055229397697i | 0.000000001-0.00000000000000001i | 0.00858412698412699+25.0656507936507i | 9999999999+9999999i | 0.00858412798412699+25.0656507936507i | -164815203.03817+250656593752.713i | 9999999999.00858+10000024.0656508i | 0.00858419081269885+25.0656507935449i | 0.00868419081269885+24.4435955641472i | 29.2 | 24.4436
[34 empty] | 29.4 | 0.0001-0.617823561170502i | 0.000000001-0.00000000000000001i | 0.00858412698412699+25.2373333333333i | 9999999999+9999999i | 0.00858412798412699+25.2373333333333i | -166532028.263314+252373419149.367i | 9999999999.00858+10000024.2373333i | 0.00858419167631191+25.2373333332263i | 0.00868419167631191+24.6195097720558i | 29.4 | 24.6195
[34 empty] | 29.6 | 0.0001-0.613649077649079i | 0.000000001-0.00000000000000001i | 0.00858412698412699+25.4090158730158i | 9999999999+9999999i | 0.00858412798412699+25.4090158730158i | -168248853.488456+254090244546.02i | 9999999999.00858+10000024.4090159i | 0.0085841925458203+25.4090158729076i | 0.0086841925458203+24.7953667952585i | 29.6 | 24.7954
[34 empty] | 29.8 | 0.0001-0.609530627463515i | 0.000000001-0.00000000000000001i | 0.00858412698412699+25.5806984126984i | 9999999999+9999999i | 0.00858412798412699+25.5806984126984i | -169965678.7136+255807069942.675i | 9999999999.00858+10000024.5806984i | 0.00858419342122341+25.5806984125891i | 0.00868419342122341+24.9711677851256i | 29.8 | 24.9712
[34 empty] | 30 | 0.0001-0.605467089947092i | 0.000000001-0.00000000000000001i | 0.00858412698412699+25.7523809523809i | 9999999999+9999999i | 0.00858412798412699+25.7523809523809i | -171682503.938742+257523895339.328i | 9999999999.00858+10000024.752381i | 0.00858419430252175+25.7523809522704i | 0.00868419430252175+25.1469138623233i | 30 | 25.1469
[34 empty] | 30.2 | 0.0001-0.601457374119627i | 0.000000001-0.00000000000000001i | 0.00858412698412699+25.9240634920634i | 9999999999+9999999i | 0.00858412798412699+25.9240634920634i | -173399329.163885+259240720735.981i | 9999999999.00858+10000024.9240635i | 0.0085841951897147+25.9240634919517i | 0.0086841951897147+25.3226061178321i | 30.2 | 25.3226
[34 empty] | 30.4 | 0.0001-0.597500417710946i | 0.000000001-0.00000000000000001i | 0.00858412698412699+26.095746031746i | 9999999999+9999999i | 0.00858412798412699+26.095746031746i | -175116154.389028+260957546132.636i | 9999999999.00858+10000025.095746i | 0.00858419608280282+26.0957460316332i | 0.00868419608280282+25.4982456139223i | 30.4 | 25.4982
[34 empty] | 30.6 | 0.0001-0.593595186222639i | 0.000000001-0.00000000000000001i | 0.00858412698412699+26.2674285714285i | 9999999999+9999999i | 0.00858412798412699+26.2674285714285i | -176832979.614171+262674371529.289i | 9999999999.00858+10000025.2674286i | 0.00858419698178598+26.2674285713144i | 0.00868419698178598+25.6738333850918i | 30.6 | 25.6738
[34 empty] | 30.8 | 0.0001-0.589740672026388i | 0.000000001-0.00000000000000001i | 0.00858412698412699+26.4391111111111i | 9999999999+9999999i | 0.00858412798412699+26.4391111111111i | -178549804.839314+264391196925.943i | 9999999999.00858+10000025.4391111i | 0.00858419788666396+26.4391111109958i | 0.00868419788666396+25.8493704389694i | 30.8 | 25.8494
[34 empty] | 31 | 0.0001-0.585935893497185i | 0.000000001-0.00000000000000001i | 0.00858412698412699+26.6107936507936i | 9999999999+9999999i | 0.00858412798412699+26.6107936507936i | -180266630.064457+266108022322.596i | 9999999999.00858+10000025.6107937i | 0.00858419879743706+26.6107936506771i | 0.00868419879743706+26.0248577571799i | 31 | 26.0249
[34 empty] | 31.2 | 0.0001-0.582179894179896i | 0.000000001-0.00000000000000001i | 0.00858412698412699+26.7824761904761i | 9999999999+9999999i | 0.00858412798412699+26.7824761904761i | -181983455.289599+267824847719.25i | 9999999999.00858+10000025.7824762i | 0.00858419971410507+26.7824761903584i | 0.00868419971410507+26.2002962961785i | 31.2 | 26.2003
[34 empty] | 31.4 | 0.0001-0.578471741987667i | 0.000000001-0.00000000000000001i | 0.00858412698412699+26.9541587301587i | 9999999999+9999999i | 0.00858412798412699+26.9541587301587i | -183700280.514742+269541673115.904i | 9999999999.00858+10000025.9541587i | 0.00858420063666796+26.9541587300398i | 0.00868420063666796+26.3756869880521i | 31.4 | 26.3757
[34 empty] | 31.6 | 0.0001-0.574810528430783i | 0.000000001-0.00000000000000001i | 0.00858412698412699+27.1258412698412i | 9999999999+9999999i | 0.00858412798412699+27.1258412698412i | -185417105.739885+271258498512.557i | 9999999999.00858+10000026.1258413i | 0.00858420156512599+27.125841269721i | 0.00868420156512599+26.5510307412902i | 31.6 | 26.551
[34 empty] | 31.8 | 0.0001-0.571195367874615i | 0.000000001-0.00000000000000001i | 0.00858412698412699+27.2975238095237i | 9999999999+9999999i | 0.00858412798412699+27.2975238095237i | -187133930.965027+272975323909.211i | 9999999999.00858+10000026.2975238i | 0.00858420249947892+27.2975238094024i | 0.00868420249947892+26.7263284415278i | 31.8 | 26.7263
[34 empty] | 32 | 0.0001-0.567625396825398i | 0.000000001-0.00000000000000001i | 0.00858412698412699+27.4692063492063i | 9999999999+9999999i | 0.00858412798412699+27.4692063492063i | -188850756.190171+274692149305.865i | 9999999999.00858+10000026.4692063i | 0.00858420343972662+27.4692063490837i | 0.00868420343972662+26.9015809522583i | 32 | 26.9016
[34 empty] | 32.2 | 0.0001-0.564099773242632i | 0.000000001-0.00000000000000001i | 0.00858412698412699+27.6408888888888i | 9999999999+9999999i | 0.00858412798412699+27.6408888888888i | -190567581.415313+276408974702.518i | 9999999999.00858+10000026.6408889i | 0.00858420438586967+27.6408888887649i | 0.00868420438586967+27.0767891155223i | 32.2 | 27.0768
[34 empty] | 32.4 | 0.0001-0.560617675876937i | 0.000000001-0.00000000000000001i | 0.00858412698412699+27.8125714285714i | 9999999999+9999999i | 0.00858412798412699+27.8125714285714i | -192284406.640457+278125800099.173i | 9999999999.00858+10000026.8125714i | 0.00858420533790742+27.8125714284463i | 0.00868420533790742+27.2519537525694i | 32.4 | 27.252
[34 empty] | 32.6 | 0.0001-0.557178303632293i | 0.000000001-0.00000000000000001i | 0.00858412698412699+27.9842539682539i | 9999999999+9999999i | 0.00858412798412699+27.9842539682539i | -194001231.865599+279842625495.826i | 9999999999.00858+10000026.984254i | 0.00858420629584043+27.9842539681276i | 0.00868420629584043+27.4270756644953i | 32.6 | 27.4271
[34 empty] | 32.8 | 0.0001-0.553780874951608i | 0.000000001-0.00000000000000001i | 0.00858412698412699+28.1559365079365i | 9999999999+9999999i | 0.00858412798412699+28.1559365079365i | -195718057.090743+281559450892.48i | 9999999999.00858+10000027.1559365i | 0.00858420725966801+28.1559365078089i | 0.00868420725966801+27.6021556328573i | 32.8 | 27.6022
[34 empty] | 33 | 0.0001-0.550424627224628i | 0.000000001-0.00000000000000001i | 0.00858412698412699+28.327619047619i | 9999999999+9999999i | 0.00858412798412699+28.327619047619i | -197434882.315885+283276276289.134i | 9999999999.00858+10000027.327619i | 0.00858420822939077+28.3276190474902i | 0.00868420822939077+27.7771944202656i | 33 | 27.7772
[34 empty] | 33.2 | 0.0001-0.547108816217251i | 0.000000001-0.00000000000000001i | 0.00858412698412699+28.4993015873015i | 9999999999+9999999i | 0.00858412798412699+28.4993015873015i | -199151707.541028+284993101685.787i | 9999999999.00858+10000027.4993016i | 0.00858420920500859+28.4993015871714i | 0.00868420920500859+27.9521927709541i | 33.2 | 27.9522
Filter Losses | [33 empty] | 33.4 | 0.0001-0.543832715521339i | 0.000000001-0.00000000000000001i | 0.00858412698412699+28.6709841269841i | 9999999999+9999999i | 0.00858412798412699+28.6709841269841i | -200868532.766171+286709927082.441i | 9999999999.00858+10000027.6709841i | 0.00858421018652121+28.6709841268527i | 0.00868421018652121+28.1271514113314i | 33.4 | 28.1272
[34 empty] | 33.6 | 0.0001-0.540595616024189i | 0.000000001-0.00000000000000001i | 0.00858412698412699+28.8426666666666i | 9999999999+9999999i | 0.00858412798412699+28.8426666666666i | -202585357.991314+288426752479.095i | 9999999999.00858+10000027.8426667i | 0.00858421117392908+28.8426666665339i | 0.00868421117392908+28.3020710505097i | 33.6 | 28.3021
Main Capacitor Losses |  | 63.5726 | Watts, 3-Phase or 217 BTUs/Hour | [30 empty] | 33.8 | 0.0001-0.537396825396826i | 0.000000001-0.00000000000000001i | 0.00858412698412699+29.0143492063492i | 9999999999+9999999i | 0.00858412798412699+29.0143492063492i | -204302183.216457+290143577875.749i | 9999999999.00858+10000028.0143492i | 0.00858421216723163+29.0143492062152i | 0.00868421216723163+28.4769523808184i | 33.8 | 28.477
Main Capacitor Fuse Losses |  | 812.8366 | Watts, 3-Phase or 2774 BTUs/Hour | [30 empty] | 34 | 0.0001-0.534235667600374i | 0.000000001-0.00000000000000001i | 0.00858412698412699+29.1860317460317i | 9999999999+9999999i | 0.00858412798412699+29.1860317460317i | -206019008.441599+291860403272.402i | 9999999999.00858+10000028.1860317i | 0.00858421316642916+29.1860317458964i | 0.00868421316642916+28.651796078296i | 34 | 28.6518
[34 empty] | 34.2 | 0.0001-0.531111482409729i | 0.000000001-0.00000000000000001i | 0.00858412698412699+29.3577142857143i | 9999999999+9999999i | 0.00858412798412699+29.3577142857143i | -207735833.666743+293577228669.057i | 9999999999.00858+10000028.3577143i | 0.00858421417152195+29.3577142855778i | 0.00868421417152195+28.8266028031681i | 34.2 | 28.8266
[34 empty] | 34.4 | 0.0001-0.528023624953858i | 0.000000001-0.00000000000000001i | 0.00858412698412699+29.5293968253968i | 9999999999+9999999i | 0.00858412798412699+29.5293968253968i | -209452658.891885+295294054065.71i | 9999999999.00858+10000028.5293968i | 0.00858421518250942+29.5293968252589i | 0.00868421518250942+29.001373200305i | 34.4 | 29.0014
[34 empty] | 34.6 | 0.0001-0.524971465272044i | 0.000000001-0.00000000000000001i | 0.00858412698412699+29.7010793650793i | 9999999999+9999999i | 0.00858412798412699+29.7010793650793i | -211169484.117028+297010879462.363i | 9999999999.00858+10000028.7010794i | 0.00858421619939206+29.7010793649401i | 0.00868421619939206+29.1761078996681i | 34.6 | 29.1761
Iron-Core Reactor Losses, 60 Hertz |  | 498.3282 | Watts, 3-Phase or 1700 BTUs/Hour | [30 empty] | 34.8 | 0.0001-0.521954387885423i | 0.000000001-0.00000000000000001i | 0.00858412698412699+29.8727619047619i | 9999999999+9999999i | 0.00858412798412699+29.8727619047619i | -212886309.342171+298727704859.018i | 9999999999.00858+10000028.8727619i | 0.00858421722216957+29.8727619046214i | 0.00868421722216957+29.350807516736i | 34.8 | 29.3508
Iron-Core Reactor Losses, (harmonic) |  | 31.1455 | Watts, 3-Phase or 106 BTUs/Hour | [30 empty] | 35 | 0.0001-0.518971791383221i | 0.000000001-0.00000000000000001i | 0.00858412698412699+30.0444444444444i | 9999999999+9999999i | 0.00858412798412699+30.0444444444444i | -214603134.567314+300444530255.671i | 9999999999.00858+10000029.0444444i | 0.00858421825084186+30.0444444443026i | 0.00868421825084186+29.5254726529194i | 35 | 29.5255
[34 empty] | 35.2 | 0.0001-0.516023088023089i | 0.000000001-0.00000000000000001i | 0.00858412698412699+30.216126984127i | 9999999999+9999999i | 0.00858412798412699+30.216126984127i | -216319959.792457+302161355652.325i | 9999999999.00858+10000029.216127i | 0.00858421928540953+30.2161269839838i | 0.00868421928540953+29.7001038959607i | 35.2 | 29.7001
Total 60 Hz Losses |  | 1374.7373 | Watts, 3-Phase or 4691 BTUs/Hour | [30 empty] | 35.4 | 0.0001-0.513107703344992i | 0.000000001-0.00000000000000001i | 0.00858412698412699+30.3878095238095i | 9999999999+9999999i | 0.00858412798412699+30.3878095238095i | -218036785.0176+303878181048.978i | 9999999999.00858+10000029.3878095i | 0.00858422032587176+30.387809523665i | 0.00868422032587176+29.87470182032i | 35.4 | 29.8747
Total Harmonic Losses |  | 31.1455 | Watts, 3-Phase or 106 BTUs/Hour | [30 empty] | 35.6 | 0.0001-0.51022507579811i | 0.000000001-0.00000000000000001i | 0.00858412698412699+30.559492063492i | 9999999999+9999999i | 0.00858412798412699+30.559492063492i | -219753610.242742+305595006445.632i | 9999999999.00858+10000029.5594921i | 0.00858422137222946+30.5594920633462i | 0.00868422137222946+30.0492669875481i | 35.6 | 30.0493
Total Harmonic Filter Losses |  | 1405.8829 | Watts, 3-Phase or 4797 BTUs/Hour | [30 empty] | 35.8 | 0.0001-0.507374656380243i | 0.000000001-0.00000000000000001i | 0.00858412698412699+30.7311746031746i | 9999999999+9999999i | 0.00858412798412699+30.7311746031746i | -221470435.467886+307311831842.286i | 9999999999.00858+10000029.7311746i | 0.00858422242448164+30.7311746030274i | 0.00868422242448164+30.2237999466472i | 35.8 | 30.2238
[34 empty] | 36 | 0.0001-0.504555908289242i | 0.000000001-0.00000000000000001i | 0.00858412698412699+30.9028571428571i | 9999999999+9999999i | 0.00858412798412699+30.9028571428571i | -223187260.693028+309028657238.939i | 9999999999.00858+10000029.9028571i | 0.0085842234826289+30.9028571427085i | 0.0086842234826289+30.3983012344193i | 36 | 30.3983
[34 empty] | 36.2 | 0.0001-0.501768306585987i | 0.000000001-0.00000000000000001i | 0.00858412698412699+31.0745396825397i | 9999999999+9999999i | 0.00858412798412699+31.0745396825397i | -224904085.918172+310745482635.594i | 9999999999.00858+10000030.0745397i | 0.00858422454667142+31.0745396823898i | 0.00868422454667142+30.5727713758038i | 36.2 | 30.5728
[34 empty] | 36.4 | 0.0001-0.499011337868481i | 0.000000001-0.00000000000000001i | 0.00858412698412699+31.2462222222222i | 9999999999+9999999i | 0.00858412798412699+31.2462222222222i | -226620911.143314+312462308032.247i | 9999999999.00858+10000030.2462222i | 0.00858422561660861+31.2462222220709i | 0.00868422561660861+30.7472108842024i | 36.4 | 30.7472
[34 empty] | 36.6 | 0.0001-0.496284499956631i | 0.000000001-0.00000000000000001i | 0.00858412698412699+31.4179047619048i | 9999999999+9999999i | 0.00858412798412699+31.4179047619048i | -228337736.368457+314179133428.901i | 9999999999.00858+10000030.4179048i | 0.0085842266924411+31.4179047617521i | 0.0086842266924411+30.9216202617955i | 36.6 | 30.9216
[34 empty] | 36.8 | 0.0001-0.493587301587302i | 0.000000001-0.00000000000000001i | 0.00858412698412699+31.5895873015873i | 9999999999+9999999i | 0.00858412798412699+31.5895873015873i | -230054561.5936+315895958825.555i | 9999999999.00858+10000030.5895873i | 0.00858422777416823+31.5895873014333i | 0.00868422777416823+31.095999999846i | 36.8 | 31.096
[34 empty] | 37 | 0.0001-0.490919262119262i | 0.000000001-0.00000000000000001i | 0.00858412698412699+31.7612698412698i | 9999999999+9999999i | 0.00858412798412699+31.7612698412698i | -231771386.818742+317612784222.208i | 9999999999.00858+10000030.7612698i | 0.00858422886179034+31.7612698411144i | 0.00868422886179034+31.2703505789951i | 37 | 31.2704
[34 empty] | 37.2 | 0.0001-0.488279911247653i | 0.000000001-0.00000000000000001i | 0.00858412698412699+31.9329523809524i | 9999999999+9999999i | 0.00858412798412699+31.9329523809524i | -233488212.043886+319329609618.862i | 9999999999.00858+10000030.9329524i | 0.00858422995530765+31.9329523807956i | 0.00868422995530765+31.4446724695479i | 37.2 | 31.4447
[34 empty] | 37.4 | 0.0001-0.485668788727612i | 0.000000001-0.00000000000000001i | 0.00858412698412699+32.1046349206349i | 9999999999+9999999i | 0.00858412798412699+32.1046349206349i | -235205037.269028+321046435015.516i | 9999999999.00858+10000031.1046349i | 0.0085842310547198+32.1046349204768i | 0.0086842310547198+31.6189661317492i | 37.4 | 31.619
[34 empty] | 37.6 | 0.0001-0.483085444106721i | 0.000000001-0.00000000000000001i | 0.00858412698412699+32.2763174603175i | 9999999999+9999999i | 0.00858412798412699+32.2763174603175i | -236921862.494172+322763260412.17i | 9999999999.00858+10000031.2763175i | 0.00858423216002705+32.2763174601579i | 0.00868423216002705+31.7932320160512i | 37.6 | 31.7932
[34 empty] | 37.8 | 0.0001-0.480529436465945i | 0.000000001-0.00000000000000001i | 0.00858412698412699+32.448i | 9999999999+9999999i | 0.00858412798412699+32.448i | -238638687.719314+324480085808.823i | 9999999999.00858+10000031.448i | 0.00858423327122906+32.447999999839i | 0.00868423327122906+31.9674705633731i | 37.8 | 31.9675
[34 empty] | 38 | 0.0001-0.478000334168755i | 0.000000001-0.00000000000000001i | 0.00858412698412699+32.6196825396826i | 9999999999+9999999i | 0.00858412798412699+32.6196825396826i | -240355512.944458+326196911205.478i | 9999999999.00858+10000031.6196825i | 0.00858423438832603+32.6196825395203i | 0.00868423438832603+32.1416822053515i | 38 | 32.1417
[34 empty] | 38.2 | 0.0001-0.475497714618134i | 0.000000001-0.00000000000000001i | 0.00858412698412699+32.7913650793651i | 9999999999+9999999i | 0.00858412798412699+32.7913650793651i | -242072338.1696+327913736602.131i | 9999999999.00858+10000031.7913651i | 0.00858423551131829+32.7913650792013i | 0.00868423551131829+32.3158673645832i | 38.2 | 32.3159
[34 empty] | 38.4 | 0.0001-0.473021164021164i | 0.000000001-0.00000000000000001i | 0.00858412698412699+32.9630476190476i | 9999999999+9999999i | 0.00858412798412699+32.9630476190476i | -243789163.394743+329630561998.784i | 9999999999.00858+10000031.9630476i | 0.00858423664020511+32.9630476188823i | 0.00868423664020511+32.4900264548611i | 38.4 | 32.49
[34 empty] | 38.6 | 0.0001-0.470570277160951i | 0.000000001-0.00000000000000001i | 0.00858412698412699+33.1347301587302i | 9999999999+9999999i | 0.00858412798412699+33.1347301587302i | -245505988.619886+331347387395.439i | 9999999999.00858+10000032.1347302i | 0.00858423777498744+33.1347301585636i | 0.00868423777498744+32.6641598814026i | 38.6 | 32.6642
[34 empty] | 38.8 | 0.0001-0.468144657175585i | 0.000000001-0.00000000000000001i | 0.00858412698412699+33.3064126984127i | 9999999999+9999999i | 0.00858412798412699+33.3064126984127i | -247222813.845029+333064212792.092i | 9999999999.00858+10000032.3064127i | 0.00858423891566419+33.3064126982446i | 0.00868423891566419+32.838268041069i | 38.8 | 32.8383
[34 empty] | 39 | 0.0001-0.465743915343915i | 0.000000001-0.00000000000000001i | 0.00858412698412699+33.4780952380953i | 9999999999+9999999i | 0.00858412798412699+33.4780952380953i | -248939639.070172+334781038188.746i | 9999999999.00858+10000032.4780952i | 0.00858424006223602+33.4780952379257i | 0.00868424006223602+33.0123513225818i | 39 | 33.0124
[34 empty] | 39.2 | 0.0001-0.463367670877875i | 0.000000001-0.00000000000000001i | 0.00858412698412699+33.6497777777778i | 9999999999+9999999i | 0.00858412798412699+33.6497777777778i | -250656464.295314+336497863585.399i | 9999999999.00858+10000032.6497778i | 0.00858424121470317+33.6497777776068i | 0.00868424121470317+33.1864101067289i | 39.2 | 33.1864
[34 empty] | 39.4 | 0.0001-0.461015550721134i | 0.000000001-0.00000000000000001i | 0.00858412698412699+33.8214603174603i | 9999999999+9999999i | 0.00858412798412699+33.8214603174603i | -252373289.520457+338214688982.053i | 9999999999.00858+10000032.8214603i | 0.00858424237306495+33.8214603172879i | 0.00868424237306495+33.3604447665668i | 39.4 | 33.3604
[34 empty] | 39.6 | 0.0001-0.458687189353856i | 0.000000001-0.00000000000000001i | 0.00858412698412699+33.9931428571429i | 9999999999+9999999i | 0.00858412798412699+33.9931428571429i | -254090114.7456+339931514378.707i | 9999999999.00858+10000032.9931429i | 0.00858424353732204+33.993142856969i | 0.00868424353732204+33.5344556676151i | 39.6 | 33.5345
[34 empty] | 39.8 | 0.0001-0.456382228603334i | 0.000000001-0.00000000000000001i | 0.00858412698412699+34.1648253968254i | 9999999999+9999999i | 0.00858412798412699+34.1648253968254i | -255806939.970743+341648339775.36i | 9999999999.00858+10000033.1648254i | 0.00858424470747366+34.16482539665i | 0.00868424470747366+33.7084431680467i | 39.8 | 33.7084
[34 empty] | 40 | 0.0001-0.454100317460317i | 0.000000001-0.00000000000000001i | 0.00858412698412699+34.336507936508i | 9999999999+9999999i | 0.00858412798412699+34.336507936508i | -257523765.195886+343365165172.015i | 9999999999.00858+10000033.3365079i | 0.00858424588352046+34.3365079363312i | 0.00868424588352046+33.8824076188709i | 40 | 33.8824
[34 empty] | 40.2 | 0.0001-0.451841111900813i | 0.000000001-0.00000000000000001i | 0.00858412698412699+34.5081904761905i | 9999999999+9999999i | 0.00858412798412699+34.5081904761905i | -259240590.421029+345081990568.668i | 9999999999.00858+10000033.5081905i | 0.00858424706546238+34.5081904760122i | 0.00868424706546238+34.0563493641114i | 40.2 | 34.0564
[34 empty] | 40.4 | 0.0001-0.449604274713185i | 0.000000001-0.00000000000000001i | 0.00858412698412699+34.6798730158731i | 9999999999+9999999i | 0.00858412798412699+34.6798730158731i | -260957415.646172+346798815965.322i | 9999999999.00858+10000033.679873i | 0.00858424825329903+34.6798730156933i | 0.00868424825329903+34.2302687409801i | 40.4 | 34.2303
[34 empty] | 40.6 | 0.0001-0.447389475330362i | 0.000000001-0.00000000000000001i | 0.00858412698412699+34.8515555555556i | 9999999999+9999999i | 0.00858412798412699+34.8515555555556i | -262674240.871315+348515641361.976i | 9999999999.00858+10000033.8515556i | 0.00858424944703098+34.8515555553743i | 0.00868424944703098+34.4041660800439i | 40.6 | 34.4042
[34 empty] | 40.8 | 0.0001-0.445196389666978i | 0.000000001-0.00000000000000001i | 0.00858412698412699+35.0232380952381i | 9999999999+9999999i | 0.00858412798412699+35.0232380952381i | -264391066.096457+350232466758.629i | 9999999999.00858+10000034.0232381i | 0.00858425064665756+35.0232380950553i | 0.00868425064665756+34.5780417053883i | 40.8 | 34.578
[34 empty] | 41 | 0.0001-0.443024699961285i | 0.000000001-0.00000000000000001i | 0.00858412698412699+35.1949206349207i | 9999999999+9999999i | 0.00858412798412699+35.1949206349207i | -266107891.321601+351949292155.283i | 9999999999.00858+10000034.1949206i | 0.00858425185217902+35.1949206347364i | 0.00868425185217902+34.7518959347751i | 41 | 34.7519
[34 empty] | 41.2 | 0.0001-0.440874094621667i | 0.000000001-0.00000000000000001i | 0.00858412698412699+35.3666031746032i | 9999999999+9999999i | 0.00858412798412699+35.3666031746032i | -267824716.546743+353666117551.937i | 9999999999.00858+10000034.3666032i | 0.00858425306359599+35.3666031744175i | 0.00868425306359599+34.9257290797958i | 41.2 | 34.9257
[34 empty] | 41.4 | 0.0001-0.438744268077601i | 0.000000001-0.00000000000000001i | 0.00858412698412699+35.5382857142858i | 9999999999+9999999i | 0.00858412798412699+35.5382857142858i | -269541541.771887+355382942948.591i | 9999999999.00858+10000034.5382857i | 0.0085842542809074+35.5382857140985i | 0.0086842542809074+35.0995414460209i | 41.4 | 35.0995
[34 empty] | 41.6 | 0.0001-0.43663492063492i | 0.000000001-0.00000000000000001i | 0.00858412698412699+35.7099682539683i | 9999999999+9999999i | 0.00858412798412699+35.7099682539683i | -271258366.997029+357099768345.244i | 9999999999.00858+10000034.7099683i | 0.00858425550411424+35.7099682537795i | 0.00868425550411424+35.2733333331446i | 41.6 | 35.2733
[34 empty] | 41.8 | 0.0001-0.434545758335232i | 0.000000001-0.00000000000000001i | 0.00858412698412699+35.8816507936509i | 9999999999+9999999i | 0.00858412798412699+35.8816507936509i | -272975192.222172+358816593741.899i | 9999999999.00858+10000034.8816508i | 0.00858425673321577+35.8816507934606i | 0.00868425673321577+35.4471050351254i | 41.8 | 35.4471
[34 empty] | 42 | 0.0001-0.432476492819349i | 0.000000001-0.00000000000000001i | 0.00858412698412699+36.0533333333334i | 9999999999+9999999i | 0.00858412798412699+36.0533333333334i | -274692017.447315+360533419138.552i | 9999999999.00858+10000035.0533333i | 0.00858425796821209+36.0533333331415i | 0.00868425796821209+35.6208568403222i | 42 | 35.6209
[34 empty] | 42.2 | 0.0001-0.430426841194613i | 0.000000001-0.00000000000000001i | 0.00858412698412699+36.2250158730159i | 9999999999+9999999i | 0.00858412798412699+36.2250158730159i | -276408842.672457+362250244535.205i | 9999999999.00858+10000035.2250159i | 0.00858425920910385+36.2250158728225i | 0.00868425920910385+35.7945890316279i | 42.2 | 35.7946
[34 empty] | 42.4 | 0.0001-0.428396525905959i | 0.000000001-0.00000000000000001i | 0.00858412698412699+36.3966984126985i | 9999999999+9999999i | 0.00858412798412699+36.3966984126985i | -278125667.897601+363967069931.859i | 9999999999.00858+10000035.3966984i | 0.00858426045589011+36.3966984125035i | 0.00868426045589011+35.9683018865975i | 42.4 | 35.9683
[34 empty] | 42.6 | 0.0001-0.426385274610626i | 0.000000001-0.00000000000000001i | 0.00858412698412699+36.568380952381i | 9999999999+9999999i | 0.00858412798412699+36.568380952381i | -279842493.122743+365683895328.513i | 9999999999.00858+10000035.568381i | 0.00858426170857191+36.5683809521845i | 0.00868426170857191+36.1419956775739i | 42.6 | 36.142
[34 empty] | 42.8 | 0.0001-0.424392820056371i | 0.000000001-0.00000000000000001i | 0.00858412698412699+36.7400634920636i | 9999999999+9999999i | 0.00858412798412699+36.7400634920636i | -281559318.347887+367400720725.167i | 9999999999.00858+10000035.7400635i | 0.00858426296714812+36.7400634918655i | 0.00868426296714812+36.3156706718091i | 42.8 | 36.3157
[34 empty] | 43 | 0.0001-0.422418899963085i | 0.000000001-0.00000000000000001i | 0.00858412698412699+36.9117460317461i | 9999999999+9999999i | 0.00858412798412699+36.9117460317461i | -283276143.573029+369117546121.82i | 9999999999.00858+10000035.911746i | 0.00858426423161941+36.9117460315464i | 0.00868426423161941+36.4893271315833i | 43 | 36.4893
[34 empty] | 43.2 | 0.0001-0.420463256907701i | 0.000000001-0.00000000000000001i | 0.00858412698412699+37.0834285714286i | 9999999999+9999999i | 0.00858412798412699+37.0834285714286i | -284992968.798172+370834371518.474i | 9999999999.00858+10000036.0834286i | 0.00858426550198602+37.0834285712275i | 0.00868426550198602+36.6629653143198i | 43.2 | 36.663
[34 empty] | 43.4 | 0.0001-0.418525638212274i | 0.000000001-0.00000000000000001i | 0.00858412698412699+37.2551111111112i | 9999999999+9999999i | 0.00858412798412699+37.2551111111112i | -286709794.023315+372551196915.128i | 9999999999.00858+10000036.2551111i | 0.00858426677824724+37.2551111109084i | 0.00868426677824724+36.8365854726961i | 43.4 | 36.8366
[34 empty] | 43.6 | 0.0001-0.416605795835153i | 0.000000001-0.00000000000000001i | 0.00858412698412699+37.4267936507937i | 9999999999+9999999i | 0.00858412798412699+37.4267936507937i | -288426619.248458+374268022311.781i | 9999999999.00858+10000036.4267937i | 0.00858426806040372+37.4267936505893i | 0.00868426806040372+37.0101878547542i | 43.6 | 37.0102
[34 empty] | 43.8 | 0.0001-0.414703486265129i | 0.000000001-0.00000000000000001i | 0.00858412698412699+37.5984761904763i | 9999999999+9999999i | 0.00858412798412699+37.5984761904763i | -290143444.473601+375984847708.436i | 9999999999.00858+10000036.5984762i | 0.00858426934845498+37.5984761902704i | 0.00868426934845498+37.1837727040053i | 43.8 | 37.1838
[34 empty] | 44 | 0.0001-0.41281847041847i | 0.000000001-0.00000000000000001i | 0.00858412698412699+37.7701587301588i | 9999999999+9999999i | 0.00858412798412699+37.7701587301588i | -291860269.698743+377701673105.089i | 9999999999.00858+10000036.7701587i | 0.00858427064240113+37.7701587299513i | 0.00868427064240113+37.3573402595328i | 44 | 37.3573
[34 empty] | 44.2 | 0.0001-0.410950513538748i | 0.000000001-0.00000000000000001i | 0.00858412698412699+37.9418412698414i | 9999999999+9999999i | 0.00858412798412699+37.9418412698414i | -293577094.923887+379418498501.743i | 9999999999.00858+10000036.9418413i | 0.00858427194224252+37.9418412696323i | 0.00868427194224252+37.5308907560935i | 44.2 | 37.5309
[34 empty] | 44.4 | 0.0001-0.409099385099384i | 0.000000001-0.00000000000000001i | 0.00858412698412699+38.1135238095239i | 9999999999+9999999i | 0.00858412798412699+38.1135238095239i | -295293920.149029+381135323898.397i | 9999999999.00858+10000037.1135238i | 0.0085842732479787+38.1135238093132i | 0.0086842732479787+37.7044244242138i | 44.4 | 37.7044
[34 empty] | 44.6 | 0.0001-0.407264858708804i | 0.000000001-0.00000000000000001i | 0.00858412698412699+38.2852063492064i | 9999999999+9999999i | 0.00858412798412699+38.2852063492064i | -297010745.374172+382852149295.05i | 9999999999.00858+10000037.2852063i | 0.00858427455960966+38.2852063489941i | 0.00868427455960966+37.8779414902853i | 44.6 | 37.8779
[34 empty] | 44.8 | 0.0001-0.40544671201814i | 0.000000001-0.00000000000000001i | 0.00858412698412699+38.456888888889i | 9999999999+9999999i | 0.00858412798412699+38.456888888889i | -298727570.599315+384568974691.704i | 9999999999.00858+10000037.4568889i | 0.00858427587713608+38.4568888886751i | 0.00868427587713608+38.051442176657i | 44.8 | 38.0514
[34 empty] | 45 | 0.0001-0.403644726631392i | 0.000000001-0.00000000000000001i | 0.00858412698412699+38.6285714285715i | 9999999999+9999999i | 0.00858412798412699+38.6285714285715i | -300444395.824458+386285800088.358i | 9999999999.00858+10000037.6285714i | 0.00858427720055708+38.628571428356i | 0.00868427720055708+38.2249267017246i | 45 | 38.2249
[34 empty] | 45.2 | 0.0001-0.401858688017979i | 0.000000001-0.00000000000000001i | 0.00858412698412699+38.8002539682541i | 9999999999+9999999i | 0.00858412798412699+38.8002539682541i | -302161221.049601+388002625485.012i | 9999999999.00858+10000037.800254i | 0.00858427852987345+38.800253968037i | 0.00868427852987345+38.398395280019i | 45.2 | 38.3984
[34 empty] | 45.4 | 0.0001-0.400088385427592i | 0.000000001-0.00000000000000001i | 0.00858412698412699+38.9719365079366i | 9999999999+9999999i | 0.00858412798412699+38.9719365079366i | -303878046.274744+389719450881.665i | 9999999999.00858+10000037.9719365i | 0.0085842798650843+38.9719365077178i | 0.0086842798650843+38.5718481222902i | 45.4 | 38.5718
[34 empty] | 45.6 | 0.0001-0.398333611807295i | 0.000000001-0.00000000000000001i | 0.00858412698412699+39.1436190476192i | 9999999999+9999999i | 0.00858412798412699+39.1436190476192i | -305594871.499887+391436276278.32i | 9999999999.00858+10000038.143619i | 0.00858428120619032+39.1436190473988i | 0.00868428120619032+38.7452854355915i | 45.6 | 38.7453
[34 empty] | 45.8 | 0.0001-0.3965941637208i | 0.000000001-0.00000000000000001i | 0.00858412698412699+39.3153015873017i | 9999999999+9999999i | 0.00858412798412699+39.3153015873017i | -307311696.72503+393153101674.973i | 9999999999.00858+10000038.3153016i | 0.0085842825531915+39.3153015870797i | 0.0086842825531915+38.9187074233589i | 45.8 | 38.9187
[34 empty] | 46 | 0.0001-0.39486984126984i | 0.000000001-0.00000000000000001i | 0.00858412698412699+39.4869841269842i | 9999999999+9999999i | 0.00858412798412699+39.4869841269842i | -309028521.950172+394869927071.626i | 9999999999.00858+10000038.4869841i | 0.00858428390608736+39.4869841267605i | 0.00868428390608736+39.0921142854907i | 46 | 39.0921
[34 empty] | 46.2 | 0.0001-0.39316044801759i | 0.000000001-0.00000000000000001i | 0.00858412698412699+39.6586666666668i | 9999999999+9999999i | 0.00858412798412699+39.6586666666668i | -310745347.175316+396586752468.281i | 9999999999.00858+10000038.6586667i | 0.0085842852648786+39.6586666664415i | 0.0086842852648786+39.2655062184239i | 46.2 | 39.2655
[34 empty] | 46.4 | 0.0001-0.391465790914066i | 0.000000001-0.00000000000000001i | 0.00858412698412699+39.8303492063493i | 9999999999+9999999i | 0.00858412798412699+39.8303492063493i | -312462172.400458+398303577864.934i | 9999999999.00858+10000038.8303492i | 0.00858428662956441+39.8303492061223i | 0.00868428662956441+39.4388834152082i | 46.4 | 39.4389
[34 empty] | 46.6 | 0.0001-0.389785680223448i | 0.000000001-0.00000000000000001i | 0.00858412698412699+40.0020317460319i | 9999999999+9999999i | 0.00858412798412699+40.0020317460319i | -314178997.625602+400020403261.588i | 9999999999.00858+10000039.0020317i | 0.00858428800014509+40.0020317458032i | 0.00868428800014509+39.6122460655798i | 46.6 | 39.6122
[34 empty] | 46.8 | 0.0001-0.388119929453262i | 0.000000001-0.00000000000000001i | 0.00858412698412699+40.1737142857144i | 9999999999+9999999i | 0.00858412798412699+40.1737142857144i | -315895822.850744+401737228658.242i | 9999999999.00858+10000039.1737143i | 0.00858428937662135+40.1737142854841i | 0.00868428937662135+39.7855943560308i | 46.8 | 39.7856
[34 empty] | 47 | 0.0001-0.386468355285376i | 0.000000001-0.00000000000000001i | 0.00858412698412699+40.345396825397i | 9999999999+9999999i | 0.00858412798412699+40.345396825397i | -317612648.075887+403454054054.896i | 9999999999.00858+10000039.3453968i | 0.00858429075899207+40.345396825165i | 0.00868429075899207+39.9589284698796i | 47 | 39.9589
[34 empty] | 47.2 | 0.0001-0.384830777508743i | 0.000000001-0.00000000000000001i | 0.00858412698412699+40.5170793650795i | 9999999999+9999999i | 0.00858412798412699+40.5170793650795i | -319329473.30103+405170879451.549i | 9999999999.00858+10000039.5170794i | 0.00858429214725808+40.5170793648458i | 0.00868429214725808+40.1322485873371i | 47.2 | 40.1322
[34 empty] | 47.4 | 0.0001-0.383207018953853i | 0.000000001-0.00000000000000001i | 0.00858412698412699+40.688761904762i | 9999999999+9999999i | 0.00858412798412699+40.688761904762i | -321046298.526172+406887704848.203i | 9999999999.00858+10000039.6887619i | 0.00858429354141885+40.6887619045267i | 0.00868429354141885+40.3055548855728i | 47.4 | 40.3056
[34 empty] | 47.6 | 0.0001-0.381596905428837i | 0.000000001-0.00000000000000001i | 0.00858412698412699+40.8604444444446i | 9999999999+9999999i | 0.00858412798412699+40.8604444444446i | -322763123.751316+408604530244.857i | 9999999999.00858+10000039.8604444i | 0.00858429494147439+40.8604444442075i | 0.00868429494147439+40.4788475387787i | 47.6 | 40.4788
[34 empty] | 47.8 | 0.0001-0.380000265657168i | 0.000000001-0.00000000000000001i | 0.00858412698412699+41.0321269841271i | 9999999999+9999999i | 0.00858412798412699+41.0321269841271i | -324479948.976458+410321355641.51i | 9999999999.00858+10000040.032127i | 0.00858429634742541+41.0321269838883i | 0.00868429634742541+40.6521267182311i | 47.8 | 40.6521
[34 empty] | 48 | 0.0001-0.37841693121693i | 0.000000001-0.00000000000000001i | 0.00858412698412699+41.2038095238097i | 9999999999+9999999i | 0.00858412798412699+41.2038095238097i | -326196774.201602+412038181038.164i | 9999999999.00858+10000040.2038095i | 0.0085842977592709+41.2038095235692i | 0.0086842977592709+40.8253925923523i | 48 | 40.8254
[34 empty] | 48.2 | 0.0001-0.37684673648159i | 0.000000001-0.00000000000000001i | 0.00858412698412699+41.3754920634922i | 9999999999+9999999i | 0.00858412798412699+41.3754920634922i | -327913599.426744+413755006434.818i | 9999999999.00858+10000040.3754921i | 0.00858429917701197+41.37549206325i | 0.00868429917701197+40.9986453267684i | 48.2 | 40.9986
[34 empty] | 48.4 | 0.0001-0.375289518562245i | 0.000000001-0.00000000000000001i | 0.00858412698412699+41.5471746031747i | 9999999999+9999999i | 0.00858412798412699+41.5471746031747i | -329630424.651887+415471831831.471i | 9999999999.00858+10000040.5471746i | 0.00858430060064741+41.5471746029308i | 0.00868430060064741+41.1718850843686i | 48.4 | 41.1719
[34 empty] | 48.6 | 0.0001-0.373745117251289i | 0.000000001-0.00000000000000001i | 0.00858412698412699+41.7188571428573i | 9999999999+9999999i | 0.00858412798412699+41.7188571428573i | -331347249.87703+417188657228.125i | 9999999999.00858+10000040.7188571i | 0.00858430203017791+41.7188571426116i | 0.00868430203017791+41.3451120253603i | 48.6 | 41.3451
[34 empty] | 48.8 | 0.0001-0.372213374967472i | 0.000000001-0.00000000000000001i | 0.00858412698412699+41.8905396825398i | 9999999999+9999999i | 0.00858412798412699+41.8905396825398i | -333064075.102173+418905482624.779i | 9999999999.00858+10000040.8905397i | 0.00858430346560381+41.8905396822925i | 0.00868430346560381+41.518326307325i | 48.8 | 41.5183
[34 empty] | 49 | 0.0001-0.370694136702299i | 0.000000001-0.00000000000000001i | 0.00858412698412699+42.0622222222224i | 9999999999+9999999i | 0.00858412798412699+42.0622222222224i | -334780900.327316+420622308021.433i | 9999999999.00858+10000041.0622222i | 0.00858430490692426+42.0622222219733i | 0.00868430490692426+41.691528085271i | 49 | 41.6915
[34 empty] | 49.2 | 0.0001-0.369187249967737i | 0.000000001-0.00000000000000001i | 0.00858412698412699+42.2339047619049i | 9999999999+9999999i | 0.00858412798412699+42.2339047619049i | -336497725.552459+422339133418.086i | 9999999999.00858+10000041.2339048i | 0.00858430635414+42.233904761654i | 0.00868430635414+41.8647175116863i | 49.2 | 41.8647
[34 empty] | 49.4 | 0.0001-0.367692564745195i | 0.000000001-0.00000000000000001i | 0.00858412698412699+42.4055873015875i | 9999999999+9999999i | 0.00858412798412699+42.4055873015875i | -338214550.777602+424055958814.741i | 9999999999.00858+10000041.4055873i | 0.0085843078072505+42.4055873013349i | 0.0086843078072505+42.0378947365897i | 49.4 | 42.0379
[34 empty] | 49.6 | 0.0001-0.366209933435739i | 0.000000001-0.00000000000000001i | 0.00858412698412699+42.57726984127i | 9999999999+9999999i | 0.00858412798412699+42.57726984127i | -339931376.002744+425772784211.394i | 9999999999.00858+10000041.5772698i | 0.00858430926625586+42.5772698410156i | 0.00868430926625586+42.2110599075799i | 49.6 | 42.2111
[34 empty] | 49.8 | 0.0001-0.364739210811499i | 0.000000001-0.00000000000000001i | 0.00858412698412699+42.7489523809525i | 9999999999+9999999i | 0.00858412798412699+42.7489523809525i | -341648201.227887+427489609608.047i | 9999999999.00858+10000041.7489524i | 0.00858431073115653+42.7489523806963i | 0.00868431073115653+42.3842131698848i | 49.8 | 42.3842
[34 empty] | 50 | 0.0001-0.363280253968253i | 0.000000001-0.00000000000000001i | 0.00858412698412699+42.9206349206351i | 9999999999+9999999i | 0.00858412798412699+42.9206349206351i | -343365026.45303+429206435004.702i | 9999999999.00858+10000041.9206349i | 0.00858431220195194+42.9206349203773i | 0.00868431220195194+42.557354666409i | 50 | 42.5574
𝐻=𝑋_𝐿/2𝜋𝑓×1000
〖𝑄_(𝑅𝐴𝑇𝐸𝐷 𝑃𝐸𝑅 𝑃𝐻𝐴𝑆𝐸) =(𝑉_(𝐶𝐴𝑃 𝑅𝐴𝑇𝐼𝑁𝐺) )^2/𝑋_𝐶 ×1000〗_
V_(CAP FUNDAMENTAL VOLTAGE)=I_(RATED FUNDAMENTAL)× X_C/1000
𝑉_(𝐶𝐴𝑃 𝐻𝐴𝑅𝑀𝑂𝑁𝐼𝐶 𝑉𝑂𝐿𝑇𝐴𝐺𝐸)=𝑋_𝐶/𝑛×𝐼_𝑛
𝐼_𝐶𝐴𝑃= 𝐼_(𝑅𝐴𝑇𝐸𝐷 𝐹𝑈𝑁𝐷𝐴𝑀𝐸𝑁𝑇𝐴𝐿)/𝑁
𝐼_(𝑅𝐸𝑆𝐼𝑆𝑇𝑂𝑅 (𝑛))=𝑋_𝐿/〖𝑅+𝑗𝑋〗_𝐿 ×𝐼_𝑛
𝐼_(𝑅𝐸𝐴𝐶𝑇𝑂𝑅 (𝑛))=𝑅/〖𝑅+𝑗𝑋〗_𝐿 ×𝐼_𝑛
𝑋_𝑒𝑓𝑓= 〖〖𝑘𝑉〗_𝐿𝐿𝑆𝑌𝑆〗^2/(𝑄_𝑒𝑓𝑓 (𝑀𝑉𝐴𝑅))×1000
𝐼_(𝐹𝐼𝐿𝑇𝐸𝑅 𝑅𝑀𝑆 𝐶𝑈𝑅𝑅𝐸𝑁𝑇)=√(∑_(𝑛=1)^𝑛▒〖𝐼_𝑛^ 〗_^2 )
(amps)
𝐼_(𝑅𝐴𝑇𝐸𝐷 𝐹𝑈𝑁𝐷𝐴𝑀𝐸𝑁𝑇𝐴𝐿)= 𝑄_𝑒𝑓𝑓/(1.73×〖〖𝑘𝑉〗_𝐿𝐿𝑆𝑌𝑆〗^ ) (amps)
𝑋_𝐶=(ℎ^2/(ℎ^2−1)) 𝑋_𝑒𝑓𝑓 (𝑜ℎ𝑚𝑠)
(ohms)
𝑋_𝐿=𝑋_𝐶/ℎ^2 (ohms)
𝐼_𝐹𝑈𝑆𝐸≥ 𝐼_𝐶𝐴𝑃×1.8
/1000
𝑉_(𝐶𝐴𝑃 𝑅𝑀𝑆 𝑉𝑂𝐿𝑇𝐴𝐺𝐸)=√(∑_(𝑛=1)^𝑛▒〖𝑉_(𝐶𝐴𝑃 𝐻𝐴𝑅𝑀𝑂𝑁𝐼𝐶 𝑉𝑂𝐿𝑇𝐴𝐺𝐸 (𝑉𝑂𝐿𝑇𝑆))〗^2 ) /1000
𝑉_(𝐶𝐴𝑃 𝑃𝐸𝐴𝐾 𝑉𝑂𝐿𝑇𝐴𝐺𝐸)=1.414 ×∑_(𝑛=1)^𝑛▒〖𝑉_(𝐶𝐴𝑃 𝐻𝐴𝑅𝑀𝑂𝑁𝐼𝐶 𝑉𝑂𝐿𝑇𝐴𝐺𝐸)〗^
/N
𝐼_(𝐶𝐴𝑃 𝑅𝑀𝑆 𝐶𝑈𝑅𝑅𝐸𝑁𝑇)=√(∑_(𝑛=1)^𝑛▒〖𝐼_𝑛^ 〗_^2 ) /N
/1000
𝑄_( 𝐶𝐴𝑃𝐴𝐶𝐼𝑇𝑂𝑅)=∑_(𝑛=1)^𝑛▒〖〖𝑋_𝑐/𝑛 𝑥 𝐼〗_𝑛^ 〗_^2 /1000

## Shunt Reactor
Rev: 10-7-2019
Northeast Power Systems, Inc.
66 Carey Road, Queensbury, NY |  |  | Phone: (518) 792-4776 Fax: (518) 792-5767 www.nepsi.com
Shunt Reactor Design
kVLLsys | 34.5 | kV
Qeff (3Ø Ouput MVAR of shunt reactor) | 12 | MVAR
f (System Frequency) | 60 | Hz
Xeff (Shunt Reactor Inductive Reactance) | 99.1875 | Ohms
H (Shunt Reactor milliHenry Rating) | 263.1108 | mH
IRATED FUNDAMENTAL CURRENT | 201.0555 | amps
Three-Phase Shunt Reactor Specification
Quantity Required: | 1
Rated Inductance: | 263.1108 | mH
Rated Impedance: | 99.1875 | Ohms
Rated Frequency: | 60 | Hz
Rated Current at Nominal Voltage: | 201.0555 | amps
Max Current at 10% Over-Voltage: | 221.1611 | amps
Qeff (3Ø Ouput MVAR of shunt reactor) | 12 | MVAR
Voltage Across Reactor at full current rating: | 19942.1965 | volts
System Voltage: | 34.5 | kV
Maximum System Voltage: | 37.95 | kV
BIL Between Winding and Ground | 150 | kV
BIL Between Terminals: | 150 | kV
Altitude: | 1000 | f.a.s.l.
Standard: | IEEE Std. C57.21
𝐼_(𝑅𝐴𝑇𝐸𝐷 𝐹𝑈𝑁𝐷𝐴𝑀𝐸𝑁𝑇𝐴𝐿)= 𝑄_𝑒𝑓𝑓/(1.73×〖〖𝑘𝑉〗_𝐿𝐿𝑆𝑌𝑆〗^2 )×1000
𝐻=𝑋_𝑒𝑓𝑓/2𝜋𝑓×1000
(amps)
𝐼_(𝑅𝐸𝑄𝑈𝐸𝑆𝑇𝐸𝐷 𝐶𝑈𝑅𝑅𝐸𝑁𝑇 𝑅𝐴𝑇𝐼𝑁𝐺)= 𝐼_(𝑅𝐴𝑇𝐸𝐷 𝐹𝑈𝑁𝐷𝐴𝑀𝐸𝑁𝑇𝐴𝐿 𝐶𝑈𝑅𝑅𝐸𝑁𝑇) ×1.1 (amps)
(Volts)
𝑉_(𝐴𝑐𝑐𝑟𝑜𝑠𝑠 𝑅𝐸𝐴𝐶𝑇𝑂𝑅)= 𝐼_(𝑅𝐸𝑄𝑈𝐸𝑆𝑇𝐸𝐷 𝐶𝑈𝑅𝑅𝐸𝑁𝑇 𝑅𝐴𝑇𝐼𝑁𝐺) ×𝑋_𝑒𝑓𝑓(Volts)
The 1.1 Multiplier on amps allows for operation at 10% Over-voltage .