## Intermittent Loading of Cables
Northeast Power Systems, Inc.
66 Carey Road, Queensbury, NY |  |  | Phone: (518) 792-4776 Fax: (518) 792-5767 www.nepsi.com
INTERMITTENT LOADING OF ELECTRIC CABLE | [6 empty] | Basis of Intermittent Loading
Required Data
Period | amps/Seconds
1 | 1327 | Amps
| 60 | Seconds |  | Equivalent RMS Current: | 593.4524 | amps
|  |  |  | Cable Utilization Factor: | 20%
2 | 1327 | Amps
| 60 | Seconds
3 | 1327 | Amps
| 60 | Seconds
4 | 1327 | Amps
| 60 | Seconds
5 | 1327 | Amps
| 60 | Seconds
6 | 1327 | Amps
| 60 | Seconds
7 | 1327 | Amps
| 60 | Seconds
8 | 1327 | Amps
| 60 | Seconds
9 | 1327 | Amps
| 60 | Seconds
10 | 1327 | Amps
| 60 | Seconds
11 | 1327 | Amps
| 60 | Seconds
12 | 1327 | Amps
| 60 | Seconds
13 | 0 | Amps
| 2880 | Seconds
Enter Current (in amps), and the Period of Time (in Seconds) for up to 13 periods of time. Off time with amps at 0 amps, and time off shall also be listed. The Equivalent RMS Amps are calculated for the total period of time.
Cable utilization factor is the ratio of the time that the cable is in use to the total time that it could be in use.
For Low Cable Utilization Factors, consideration should be given to using long barrelled lugs, 2-hole and 4-hole lugs when available, and 4-hole bus connections.

## Short Time Current Rating
Northeast Power Systems, Inc.
66 Carey Road, Queensbury, NY |  | Phone: (518) 792-4776 Fax: (518) 792-5767 www.nepsi.com
Short Time Current Rating of Conductor |  |  | Cable/Conductor Rating
|  |  | AWG/MCM | Diameter (Inches) | Circular Mils | Area (mm2) | Diameter (mm)
|  |  | 25 | 0.0179 | 320.4 | 0.162 | 0.455
Copper Conductors - Calculation of Time |  |  | 24 | 0.0201 | 404 | 0.205 | 0.511
1000000 | A = Conductor area - cmils |  | 23 | 0.0226 | 509.5 | 0.258 | 0.573
1327 | I= Short Circuit/Overload Current - RMS Amps |  | 22 | 0.0253 | 642.4 | 0.326 | 0.644
| T1 = Operating Temperature (degree C) |  | 21 | 0.0285 | 810.1 | 0.41 | 0.723
60 | T2 = Maximum Temperature (degree C) |  | 20 | 0.032 | 1022 | 0.518 | 0.812
#VALUE! | t = Time of Short Circuit or Overload Load Current (in seconds) |  | 17 | 0.0453 | 2048 | 1.04 | 1.15
|  |  | 16 | 0.0508 | 2583 | 1.31 | 1.29
|  |  | 15 | 0.0571 | 3257 | 1.65 | 1.45
Copper Conductors - Calculation of Cmils |  |  | 14 | 0.0641 | 4107 | 2.08 | 1.63
64879.0724 | A = Conductor area - cmils |  | 13 | 0.072 | 5178 | 2.62 | 1.83
1327 | I= Short Circuit Current - RMS Amps |  | 12 | 0.0808 | 6530 | 3.31 | 2.05
50 | T1 = Operating Temperature (degree C) |  | 11 | 0.0907 | 8234 | 4.17 | 2.31
100 | T2 = Maximum Temperature (degree C) |  | 10 | 0.102 | 10383 | 5.26 | 2.59
5 | t = Time of Short Circuit or Overload Current (in seconds) |  | 9 | 0.114 | 13092 | 6.63 | 2.91
|  |  | 8 | 0.128 | 16509 | 8.37 | 3.26
|  |  | 7 | 0.144 | 20818 | 10.5 | 3.67
|  |  | 6 | 0.162 | 26251 | 13.3 | 4.12
|  |  | 5 | 0.182 | 33101 | 16.8 | 4.62
|  |  | 4 | 0.204 | 41740 | 21.2 | 5.19
Aluminum Conductors - Calculation of Time |  |  | 3 | 0.229 | 52633 | 26.7 | 5.83
500000 | A = Conductor area - cmils |  | 2 | 0.258 | 66369 | 33.6 | 6.54
2042 | I= Short Circuit Current - RMS Amps |  | 1 | 0.289 | 83690 | 42.4 | 7.35
60 | T1 = Operating Temperature (degree C) |  | 0 | 0.325 | 105531 | 53.5 | 8.25
90 | T2 = Maximum Temperature (degree C) |  | 00 | 0.365 | 133072 | 67.4 | 9.27
32.252 | t = Time of Short Circuit or Load Current (in seconds) |  | 000 | 0.41 | 167800 | 85 | 10.4
|  |  | 0000 | 0.46 | 211592 | 107 | 11.7
|  |  | 250 | 0.5 | 250000 | 126.6772 | 12.7
|  |  | 300 | 0.548 | 300000 | 152.1666 | 13.9192
|  |  | 350 | 0.592 | 350000 | 177.5831 | 15.0368
|  |  | 400 | 0.632 | 400000 | 202.3916 | 16.0528
|  |  | 450 | 0.671 | 450000 | 228.141 | 17.0434
|  |  | 500 | 0.707 | 500000 | 253.2778 | 17.9578
|  |  | 600 | 0.775 | 600000 | 304.3419 | 19.685
|  |  | 700 | 0.837 | 700000 | 354.9844 | 21.2598
299.5413 | t = Time of Short Circuit - 0.01 to 10 seconds |  | 750 | 0.866 | 750000 | 380.0092 | 21.9964
|  |  | 800 | 0.894 | 800000 | 404.9798 | 22.7076
|  |  | 900 | 0.949 | 900000 | 456.3423 | 24.1046
|  |  | 1000 | 1 | 1000000 | 506.7087 | 25.4
|  |  | 1250 | 1.118 | 1250000 | 633.3473 | 28.3972
Bus Bar Rating
|  |  | AWG | Width (Inches) | Circular Mils | Area (inches2) | Thickness (Inches)
|  |  | 1/4 x 1" | 1 | 196350 | 0.25 | 0.25 | about 000
|  |  | 1/4 x 2" | 2 | 785400 | 0.5 | 0.25
|  |  | 1/4 x 3" | 3 | 1767150 | 0.75 | 0.25
|  |  | 1/2 x 2" | 2 | 1570800 | 1 | 0.5
|  |  | 1/2 x 3" | 3 | 3534300 | 1.5 | 0.5